## Revisions
Andover (JC)
Station Phone:
Station Address:
EMS Information
RTU Name: | ANDOVR | ASE SPT Physical Communication Ports
FEP: | RF0 | Communication
Channel: | 43 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10186 | Port 1: | DNP | 10186 | 10 | JC EMS 9600 Baud | CDMA Dedicated
|  | Port 2: | Not used
RTU Information |  | Port 3: | CDC2 | 30 | 3 | RTU, 1200 baud | RS232/Modem
RTU Type: | CDC 44-550 | Port 4: | Not used
Firmware:
Powered At: | 48 VDC
Peripherals: | -
|  |  |  | Rev | Date | Description | Rev. By
|  |  |  | A | 2018-08-30 | Converted to Excel format. RTU being converted to DNP and cutover to CDMA dedicated circuit via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF2C021). Added SPT Comm Fail status and spared the A/D Calibration analog points not needed for DNP. LCR SAP# 15730680. Config: ANDOVR Rev A | HFR/BMcD
|  |  |  | B | 2018-09-18 | Created ASE Protocol Config based on points list rev A. Config: Andover Rev A | A.Shafer/BMcD

## Control
|  | Update: | 8/30/2018 | [7 empty] | RTU Type: | CDC 44-550
Andover (JC)
Pt. Own | DNP to EMS |  | RTU |  |  | Device type | CDC II to RTU |  | Card Slot | RTU
| Type | Pt. | Point Description | kV | Function |  | Seq No. | Relay No. |  | Interconnection | Customer Termination | Comments | Rev
| C | 0 | E707-1 LBSW | 34.5 | CLOSE | CTRL | 0 | K0C |  | DO-1 | TB1-3,6 |  | A
| C |  | E707-1 LBSW | 34.5 | OPEN | CTRL | 0 | K0T |  | DO-1 | TB2-3,6 |  | A
| C | 1 | NO 9 LBSW | 34.5 | CLOSE | CTRL | 1 | K1C |  | DO-1 | TB1-9,12 |  | A
| C |  | NO 9 LBSW | 34.5 | OPEN | CTRL | 1 | K1T |  | DO-1 | TB2-9,12 |  | A
| C | 2 | E707-2 LBSW | 34.5 | CLOSE | CTRL | 2 | K2C |  | DO-1 | TB1-15,18 |  | A
| C |  | E707-2 LBSW | 34.5 | OPEN | CTRL | 2 | K2T |  | DO-1 | TB2-15,18 |  | A
| C | 3 | BK 1 FUT OCB | 34.5/12 | CLOSE | CTRL | 3 | K3C |  | DO-1 | TB1-21,24 |  | A
| C |  | BK 1 FUT OCB | 34.5/12 | OPEN | CTRL | 3 | K3T |  | DO-1 | TB2-21,24 |  | A
| C | 4 | 14704 OCB | 12.5 | CLOSE | CTRL | 4 | K4C |  | DO-1 | TB1-27.30 |  | A
| C |  | 14704 OCB | 12.5 | OPEN | CTRL | 4 | K4T |  | DO-1 | TB2-27,30 |  | A
| C | 5 | 14705 OCB | 12/5 | CLOSE | CTRL | 5 | K5C |  | DO-1 | TB1-33,36 |  | A
| C |  | 14705 OCB | 12.5 | OPEN | CTRL | 5 | K5T |  | DO-1 | TB2-33,36 |  | A
| C | 6 | 14706 OCB | 12.5 | CLOSE | CTRL | 6 | K6C |  | DO-1 | TB1-39,42 |  | A
| C |  | 14706 OCB | 12.5 | OPEN | CTRL | 6 | K6T |  | DO-1 | TB2-39,42 |  | A
| C | 7 | BK 2 VCB | 34.5/12 | CLOSE | CTRL | 7 | K7C |  | DO-1 | TB1-45,48 |  | A
| C |  | BK 2 VCB | 34.5/12 | OPEN | CTRL | 7 | K7T |  | DO-1 | TB2-45,48 |  | A
| C | 8 | 17702 VCB | 12.5 | CLOSE | CTRL | 8 | K0C |  | DO-2 | TB1-3,6 |  | A
| C |  | 17702 VCB | 12.5 | OPEN | CTRL | 8 | K0T |  | DO-2 | TB2-3,6 |  | A
| C | 9 | 17703 VCB | 12.5 | CLOSE | CTRL | 9 | K1C |  | DO-2 | TB1-9,12 |  | A
| C |  | 17703 VCB | 12.5 | OPEN | CTRL | 9 | K1T |  | DO-2 | TB2-9,12 |  | A
| C | 10 | ADAPTIVE RELAYING |  | ON | CTRL | 0A | K2C |  | DO-2 | TB1-15,18 |  | A
| C |  | ADAPTIVE RELAYING |  | OFF | CTRL | 0A | K2T |  | DO-2 | TB2-15,18 |  | A
| C | 11 | SPARE |  |  | CTRL | 0B | K3C |  | DO-2 | TB1-21,24 | Updated to match EMS, was CAP 1 OCB (Spare) in old pt list. | A
| C |  | SPARE |  |  | CTRL | 0B | K3T |  | DO-2 | TB2-21,24 |  | A
| C | 12 | SPARE |  |  | CTRL | 0C | K4C |  | DO-2 | TB1-27.30 |  | A
| C |  | SPARE |  |  | CTRL | 0C | K4T |  | DO-2 | TB2-27,30 |  | A
| C | 13 | SPARE |  |  | CTRL | 0D | K5C |  | DO-2 | TB1-33,36 |  | A
| C |  | SPARE |  |  | CTRL | 0D | K5T |  | DO-2 | TB2-33,36 |  | A
| C | 14 | SPARE |  |  | CTRL | 0E | K6C |  | DO-2 | TB1-39,42 |  | A
| C |  | SPARE |  |  | CTRL | 0E | K6T |  | DO-2 | TB2-39,42 |  | A
| C | 15 | CAP 2 B6 GCB | 34.5 | CLOSE | CTRL | 0F | K7C |  | DO-2 | TB1-45,48 |  | A
| C |  | CAP 2 B6 GCB | 34.5 | OPEN | CTRL | 0F | K7T |  | DO-2 | TB2-45,48 |  | A

## Status
| Update: | 8/8/2018 | [6 empty] | RTU Type: | CDC 44-550
Andover (JC)
Pt. | DNP to EMS |  |  |  |  | CDC II to RTU
Own | Type | Pt. | Point Description | kV | Function | Type | Seq. | Bit | Card Slot | Inter-Connection | Customer Termination | Comments | Rev
| I | 0 | LOCAL/REMOTE |  | LOC/REM | SS | 30 | 0 |  | DI-1 | TB1-1,2 |  | A
| I | 1 | BATTERY |  | NM/ALM | SS | 30 | 1 |  | DI-1 | TB1-4,5 |  | A
| I | 2 | E707-1 LBSW | 34.5 | OP/CL | SS | 30 | 2 |  | DI-1 | TB1-6,7 |  | A
| I | 3 | E707-1 LBSW | 34.5 | OP/CL | SS | 30 | 3 |  | DI-1 | TB1-9,10 |  | A
| I | 4 | NO 9 LBSW | 34.5 | OP/CL | SS | 30 | 4 |  | DI-1 | TB1-11,22 |  | A
| I | 5 | NO 9 LBSW | 34.5 | OP/CL | SS | 30 | 5 |  | DI-1 | TB1-14,15 |  | A
| I | 6 | E707-2 LBSW | 34.5 | OP/CL | SS | 30 | 6 |  | DI-1 | TB1-16,17 |  | A
| I | 7 | E707-2 LBSW | 34.5 | OP/CL | SS | 30 | 7 |  | DI-1 | TB1-19,20 |  | A
| I | 8 | CAP2 RELAY FAIL | 34.5 | NM/ALM | SS | 30 | 8 |  | DI-1 | TB2-1,2 |  | A
| I | 9 | CAP2 PART. FAIL ALM | 34.5 | NM/ALM | SS | 30 | 9 |  | DI-1 | TB2-4,5 |  | A
| I | 10 | CAP2GCB LO GAS ALM | 34.5 | NM/ALM | SS | 30 | 10 |  | DI-1 | TB2-6,7 |  | A
| I | 11 | CAP2 NEUT UNBAL ALM | 34.5 | NM/ALM | SS | 30 | 11 |  | DI-1 | TB2-9,10 |  | A
| I | 12 | CAP2 OVERTEMP ALM | 34.5 | NM/ALM | SS | 30 | 12 |  | DI-1 | TB2-11,22 |  | A
| I | 13 | ADAPTIVE RELAYING - |  | OFF/ON | SS | 30 | 13 |  | DI-1 | TB2-14,15 |  | A
| I | 14 | BK 1 OIL SPILL | 34.5 | NM/ALM | SS | 30 | 14 |  | DI-1 | TB2-16,17 |  | A
| I | 15 | BK 2 ALARMS | 34.5 | NM/ALM | SS | 30 | 15 |  | DI-1 | TB2-19,20 |  | A
| C&I | 16 | BK 1 FUT OCB | 34.5 | OP/CL | 2B | 0 | 0,8 |  | D1-2 | TB1-1,2 |  | A
| C&I | 17 | 14704 OCB | 12.5 | OP/CL | 2B | 0 | 1,9 |  | D1-2 | TB1-4,5 |  | A
| C&I | 18 | 14705 OCB | 12.5 | OP/CL | 2B | 0 | 2,10 |  | D1-2 | TB1-6,7 |  | A
| C&I | 19 | 14706 OCB | 12.5 | OP/CL | 2B | 0 | 3,11 |  | D1-2 | TB1-9,10 |  | A
| C&I | 20 | BK 2 VCB | 12.5 | OP/CL | 2B | 0 | 4,12 |  | D1-2 | TB1-11,12 |  | A
| C&I | 21 | 17702 VCB | 12.5 | OP/CL | 2B | 0 | 5,13 |  | D1-2 | TB1-14,15 |  | A
| C&I | 22 | 17703 VCB | 12.5 | OP/CL | 2B | 0 | 6,14 |  | D1-2 | TB1-16,17 |  | A
| C&I | 23 | SPARE |  |  | 2B | 0 | 7,15 |  | D1-2 | TB1-19,20 |  | A
| C&I | 24 | SPARE |  |  | 2B | 1 | 0,8 |  | D1-2 | TB2-1,2 |  | A
| C&I | 25 | SPARE | 21 | NM/ALM | 2B | 1 | 1,9 |  | D1-2 | TB2-4,5 |  | A
| C&I | 26 | SPARE | 21 | NM/ALM | 2B | 1 | 2,10 |  | D1-2 | TB2-6,7 |  | A
| C&I | 27 | BK 2 Tank Pressure (Nitrogen) | 21 | NM/ALM | 2B | 1 | 3,11 |  | D1-2 | TB2-9,10 |  | A
| C&I | 28 | CAP2 BKR (10 B 6) | 34.5 | OP/CL | 2B | 1 | 4,12 |  | D1-2 | TB2-11,12 |  | A
| C&I | 29 | CAP2 27/59X TRIP ALM | 34.5 | NM/ALM | 2B | 1 | 5,13 |  | D1-2 | TB2-14,15 |  | A
| C&I | 30 | SPARE |  |  | 2B | 1 | 6,14 |  | D1-2 | TB2-16,17 |  | A
| C&I | 31 | SPARE |  |  | 2B | 1 | 7,15 |  | D1-2 | TB2-19,20 |  | A
| I | 32 | SPT COMM FAIL |  | NM/ALM | SPT INTERNAL INDICATION | [5 empty] | New point | A

## Analog
| Update: | 8/8/2018 | [7 empty] | RTU Type: | CDC 44-550
Andover (JC)
Pt. | DNP To EMS |  |  | RTU | Full | CDC II to EMS |  | Card | RTU Cabinet | XDCR Cabinet
Own | Type | Pt. | Point Description | kV | Scale | Type | Seq. | Slot | Termination | Termination | Comments | Rev
| AI | 0 | SPARE |  |  | CNTS | 80 |  |  |  | CDC II FULL SCALE Calibration, keep index spare. | A
| AI | 1 | SPARE |  |  | CNTS | 81 |  |  |  | CDC II ZERO SCALE Calibration, keep index spare. | A
| AI | 2 | BK 1 MW | 34.5/12 | 43.2 |  | 82 | 2 | AI-1 | TB-1-1,2 |  | A
| AI | 3 | BK 1 MVAR | 34.5/12 | 43.2 |  | 83 | 2 | AI-1 | TB-1-4,5 |  | A
| AI | 4 | BK 2 MW | 34.5/12 | 15.59 |  | 84 | 2 | AI-1 | TB-1-7,8 |  | A
| AI | 5 | BK 2 MVAR | 34.5/12 | 15.59 |  | 85 | 2 | AI-1 | TB-1-10,11 |  | A
| AI | 6 | SPARE |  |  |  | 86 | 2 | AI-1 | TB-2-1,2 |  | A
| AI | 7 | CAP BANK #2 VOLTS | 34.5 | 45 |  | 87 | 2 | AI-1 | TB-2-4,5 |  | A
| AI | 8 | SPARE |  |  |  | 88 | 2 | AI-1 | TB-2-7,8 |  | A
| AI | 9 | SPARE |  |  |  | 89 | 2 | AI-1 | TB-2-10,11 |  | A
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)