## Revisions
Colts Neck (JC)
|  |  | Station Phone: |  | 732-780-6326
|  |  | Latitude: |  | 40° 17’ 23”
EMS Information |  |  | Longitude: |  | 74° 10’ 28”
RTU Name: | COLTS_NK | ASE SPT Physical Communication Ports
FEP: | RF21 | Communication
Channel: | 78 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10240 | Port 1: | DNP | 10240 | 10 | FE East EMS 9600 Baud | Cellular IP
|  | Port 2: | Not used
PLC Information |  | Port 3: | CDC2 | 30 | 2 | RTU, 1200 baud | RS232/Modem
Processor Type: | N/A | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | 8890 via ASE Protocol Translator
Size:
Powered At: |  |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-08-05 | Converted to Excel format. RTU being converted to DNP and cutover to Cellular IP via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF2 CH49). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted. WO# 16049175. SCORES ID 104848. Reviewed by H. Riley/BMcD | J.McLaughlin (BMcD)
|  |  |  | B | 2019-09-04 | Built ASE SPT configuration. SPT Configuration: COLTS NECK ASE SPT CDC2 DNP Rev A | M.Smith (BMcD)

## Control
| Update: | 2019-08-05 | [7 empty] | RTU Type: | 8890 via ASE Protocol Translator
Colts Neck (JC)
DNP to EMS |  | RTU |  |  | Device type | CDC2 to RTU |  | Card Slot | RTU Cabinet
Type | Pt | Point Description | kV | Function |  | Seq No. | Relay No. |  | Inter-connection | Customer Termination | Comments | Rev
C | 0 | M139-1 LBSW | 34.5 | CLOSE | CTRL | 0 | K0C |  | DO-1 | TB1-3,6
C |  | M139-1 LBSW | 34.5 | OPEN | CTRL | 0 | K0T |  | DO-1 | TB2-3,6
C | 1 | NO 6 LBSW | 34.5 | CLOSE | CTRL | 1 | K1C |  | DO-1 | TB1-9,12
C |  | NO 6 LBSW | 34.5 | OPEN | CTRL | 1 | K1T |  | DO-1 | TB2-9,12
C | 2 | M139-2 LBSW | 34.5 | CLOSE | CTRL | 2 | K2C |  | DO-1 | TB1-15,18
C |  | M139-2 LBSW | 34.5 | OPEN | CTRL | 2 | K2T |  | DO-1 | TB2-15,18
C | 3 | BK 1 VCB | 34.5/12 | CLOSE | CTRL | 3 | K3C |  | DO-1 | TB1-21,24
C |  | BK 1 VCB | 34.5/12 | OPEN | CTRL | 3 | K3T |  | DO-1 | TB2-21,24
C | 4 | BT VCB | 12.5 | CLOSE | CTRL | 4 | K4C |  | DO-1 | TB1-27.30
C |  | BT VCB | 12.5 | OPEN | CTRL | 4 | K4T |  | DO-1 | TB2-27,30
C | 5 | 47426 VCB | 12.5 | CLOSE | CTRL | 5 | K5C |  | DO-1 | TB1-33,36
C |  | 47426 VCB | 12.5 | OPEN | CTRL | 5 | K5T |  | DO-1 | TB2-33,36
C | 6 | 47427 VCB | 12.5 | CLOSE | CTRL | 6 | K6C |  | DO-1 | TB1-39,42
C |  | 47427 VCB | 12.5 | OPEN | CTRL | 6 | K6T |  | DO-1 | TB2-39,42
C | 7 | BK 2 VCB | 34.5/12.5 | CLOSE | CTRL | 7 | K7C |  | DO-1 | TB1-45,48
C |  | BK 2 VCB | 34.5/12.5 | OPEN | CTRL | 7 | K7T |  | DO-1 | TB2-45,48
C | 8 | 47428 VCB |  | CLOSE | CTRL | 8 | K0C |  | DO-2 | TB1-3,6
C |  | 47428 VCB |  | OPEN | CTRL | 8 | K0T |  | DO-2 | TB2-3,6
C | 9 | 47429 VCB |  | CLOSE | CTRL | 9 | K1C |  | DO-2 | TB1-9,12
C |  | 47429 VCB |  | OPEN | CTRL | 9 | K1T |  | DO-2 | TB2ADAPTVIE
C | 10 | ADAPTIVE RELAYING |  | ON | CTRL | 0A | K2C |  | DO-2 | TB1-15,18
C |  | ADAPTIVE RELAYING |  | OFF | CTRL | 0A | K2T |  | DO-2 | TB2-15,18
C | 11 | 5PCT VOLT RED |  | ON | CTRL | 0B | K3C |  | DO-2 | TB1-21,24
C |  | 5PCT VOLT RED |  | OFF | CTRL | 0B | K3T |  | DO-2 | TB2-21,24
C | 12 | Undefined |  |  | INFORMATION MISSING FROM ORIGINAL PT LIST | [5 empty] | Updated to match EMS | A
C |  | Undefined | [8 empty] | Updated to match EMS | A
C | 13 | Undefined | [8 empty] | Updated to match EMS | A
C |  | Undefined | [8 empty] | Updated to match EMS | A
C | 14 | Undefined | [8 empty] | Updated to match EMS | A
C |  | Undefined | [8 empty] | Updated to match EMS | A
C | 15 | Undefined | [8 empty] | Updated to match EMS | A
C |  | Undefined | [8 empty] | Updated to match EMS | A

## Status
| Update: | 2019-08-05 | [6 empty] | RTU Type: | 8890 via ASE Protocol Translator
Colts Neck (JC)
Pt. | DNP TO EMS |  |  |  |  | CDC2 to RTU |  |  | Card Slot | RTU Cabinet
Own | Type | Pt. | Point Description | kV | Function | Type | Seq. | Bit |  | Inter-Connection | Customer Termination | Comments | Rev
| I | 0 | LOCAL/REMOTE |  | LOC/REM | SS | 30 | 0 |  | DI-1 | TB1-1,2
| I | 1 | BATTERY |  | NM/ALM | SS | 30 | 1 |  | DI-1 | TB1-4,5
| I | 2 | M139-1 LBSW | 34.5 | CL/OP | SS | 30 | 2 |  | DI-1 | TB1-6,7
| I | 3 | M139-1 LBSW | 34.5 | OP/CL | SS | 30 | 3 |  | DI-1 | TB1-9,10
| I | 4 | NO 6 LBSW | 34.5 | CL/OP | SS | 30 | 4 |  | DI-1 | TB1-11,22
| I | 5 | NO 6 LBSW | 34.5 | OP/CL | SS | 30 | 5 |  | DI-1 | TB1-14,15
| I | 6 | M139-2 LBSW | 34.5 | CL/OP | SS | 30 | 6 |  | DI-1 | TB1-16,17
| I | 7 | M139-2 LBSW | 34.5 | OP/CL | SS | 30 | 7 |  | DI-1 | TB1-19,20
| I | 8 | BK 1 | 2.8333 | NM/ALM | SS | 30 | 8 |  | DI-1 | TB2-1,2
| I | 9 | BK 2 | 2.8333 | NM/ALM | SS | 30 | 9 |  | DI-1 | TB2-4,5
| I | 10 | ADAPTIVE RELAYING |  | OFF/ON | SS | 30 | 10 |  | DI-1 | TB2-6,7
| I | 11 | 5PCT VOLT RED |  | OFF/ON | SS | 30 | 11 |  | DI-1 | TB2-9,10
| I | 12 | SPARE |  |  | SS | 30 | 12 |  | DI-1 | TB2-11,22
| I | 13 | SPARE |  |  | SS | 30 | 13 |  | DI-1 | TB2-14,15
| I | 14 | SPARE |  |  | SS | 30 | 14 |  | DI-1 | TB2-16,17
| I | 15 | SPARE |  |  | SS | 30 | 15 |  | DI-1 | TB2-19,20
| C&I | 16 | BK 1 VCB | 34/12 | OP/CL | 2B | 0 | 0,8 |  | D1-2 | TB1-1,2
| C&I | 17 | BT VCB | 12 | OP/CL | 2B | 0 | 1,9 |  | D1-2 | TB1-4,5
| C&I | 18 | 47426 VCB | 12 | OP/CL | 2B | 0 | 2,10 |  | D1-2 | TB1-6,7
| C&I | 19 | 47427 VCB | 12 | OP/CL | 2B | 0 | 3,11 |  | D1-2 | TB1-9,10
| C&I | 20 | BK 2 VCB | 34.5/12 | OP/CL | 2B | 0 | 4,12 |  | D1-2 | TB1-11,12
| C&I | 21 | 47428 VCB | 12 | OP/CL | 2B | 0 | 5,13 |  | D1-2 | TB1-14,15
| C&I | 22 | 47429 VCB | 12 | OP/CL | 2B | 0 | 6,14 |  | D1-2 | TB1-16,17
| C&I | 23 | SPARE |  |  | 2B | 0 | 7,15 |  | D1-2 | TB1-19,20
| I | 24 | SPT COMM FAIL |  | NM/ALM | SPT INTERNAL INDICATION | [5 empty] | New pt | A

## Analog
| Update: | 2019-08-05 | [7 empty] | RTU Type: | 8890 via ASE Protocol Translator
Colts Neck (JC)
Pt. | DNP to EMS |  |  |  | CDC2 to RTU |  | DEVICE | Card | RTU | XDCR
Own | Type | Pt. | Point Description | kV | Seq. No. | Full Scale | TYPE | Slot | Cabinet Termination | Cabinet Termination | Comments | Rev
| AI | 0 | SPARE |  | 80 |  | CNTS |  |  |  | 100PCT A/D CAL. Keep index spare. | A
| AI | 1 | SPARE |  | 81 |  | CNTS |  |  |  | 0PCT A/D CAL. Keep index spare. | A
| AI | 2 | BANK 2 MW | 12.5 | 82 | 25.92 | MW |  | TB-1-1,2
| AI | 3 | BANK 2 MVAR | 12.5 | 83 | 25.92 | MX |  | TB-1-4,5
| AI | 4 | BANK 2 kV | 12.5 | 84 | 15.59 | kV |  | TB-1-6,7
| AI | 5 | BANK 1 MW | 12.5 | 85 | 25.92 | MW |  | TB-1-9,10
| AI | 6 | BANK 1 MVAR | 12.5 | 86 | 25.92 | MX |  | TB-1-11,12
Points not mapped to EMS
|  |  | SPARE |  | 87 |  |  |  | TB-1-14,15
|  |  | SPARE |  | 88 |  |  |  | TB-1-16,17
|  |  | SPARE |  | 89 |  |  |  | TB-1-19,20