## Revisions
Gore Junction 115kV Substation (PN)
|  |  | Location: | Location: | 4902 Old Zuck Road, Erie, PA 16506-4966
Phone:
|  |  | Latitude: |  | 42.0699
EMS Information |  |  | Longitude: |  | -80.1232
RTU Name: | GORE_JCT | ASE SPT Physical Communication Ports
FEP: | RF7 | Communication
Channel: | 10 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 20289 | Port 1: | DNP | 20289 | 10 | FE EAST EMS 38400 Baud | MPLS
|  | Port 2: | Not used
PLC Information |  | Port 3: | CDC2 | 30 | 2 | RTU, 1200 baud | RS232/Modem
Processor Type: |  | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | CDC 44-550 with ASE Protocol Translator
Size:
Powered At: |  |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-03-20 | Converted to Excel format. RTU being converted to DNP and cutover to MPLS, updated baud rate and FEP/CH (old FEP/CH JF2 CH018). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted in red. WO#15834643 Scores I.D.103413. Reviewed by H. Riley/BMcD | T. Belshe (BMcD)
|  |  |  | B | 2019-05-07 | Updated to add DC GND Detect for the Battery Charger replacement occuring with the MPLS project in rev A. WO#15834643 Scores ID 103413. | H. Riley (BMcD)
|  |  |  | C | 2019-06-04 | Created config. Config: Gore Junction ASE SPT CDC2 DNP Rev A.xml, WO#15834643 Scores ID 103413. | M.Smith/BMcD

## Control
| Update: | 2019-03-20 | [7 empty] | RTU Type: | CDC 44-550 with ASE Protocol Translator
Gore Junction 115kV Substation (PN)
DNP to EMS |  | RTU |  |  | CDC2 to RTU | Basket Card Digital Output Driver |  |  | Wall Card Relay Output
Type | Pt | Point Description | kV | Function | Seq No | Card Sw | Card Loc | Card Conn | Wall Pos. | Relay | Close Relay | Trip Relay | Terminal Numbers | Comments | Rev
C | 0 | Erie S.-Green Gardn 115 kV CB | 115 | CLOSE | 0 | S3 | 4 | J3 | B1 | K0 | TB1 |  | 2-6
C |  |  |  | OPEN | [7 empty] | TB2
C | 1 | Rolling Meadows 115 kV MOABS | 115 | CLOSE | 1 | S3 | 4 | J3 | B1 | K1 | TB1 |  | 8-12
C |  |  |  | OPEN | [7 empty] | TB2
C | 2 | Fairview East 115 kV CB | 115 | CLOSE | 2 | S3 | 4 | J3 | B1 | K2 | TB1 |  | 14-18
C |  |  |  | OPEN | [7 empty] | TB2
C | 3 | Relay Communications Reset |  | AL | 3 | S3 | 4 | J3 | B1 | K3 | TB1 |  | 20-24
C |  |  |  | NM | [7 empty] | TB2
C | 4 | Spare |  |  | 4 | S3 | 4 | J3 | B1 | K4 | TB1 |  | 26-30
C | [11 empty] | TB2
C | 5 | Spare |  |  | 5 | S3 | 4 | J3 | B1 | K5 | TB1 |  | 32-36
C | [11 empty] | TB2
C | 6 | Spare |  |  | 6 | S3 | 4 | J3 | B1 | K6 | TB1 |  | 38-42
C | [11 empty] | TB2
C | 7 | Spare |  |  | 7 | S3 | 4 | J3 | B1 | K7 | TB1 |  | 44-48
C | [11 empty] | TB2
Points in RTU not mapped to EMS
|  | Spare |  |  | 8 | S2 | 4 | J2 | B2 | K0 | TB1 | TB2 | 2-6
|  | Spare |  |  | 9 | S2 | 4 | J2 | B2 | K1 | TB1 | TB2 | 8-12
|  | Spare |  |  | 0A | S2 | 4 | J2 | B2 | K2 | TB1 | TB2 | 14-18
|  | Spare |  |  | 0B | S2 | 4 | J2 | B2 | K3 | TB1 | TB2 | 20-24
|  | Spare |  |  | 0C | S2 | 4 | J2 | B2 | K4 | TB1 | TB2 | 26-30
|  | Spare |  |  | 0D | S2 | 4 | J2 | B2 | K5 | TB1 | TB2 | 32-36
|  | Spare |  |  | 0E | S2 | 4 | J2 | B2 | K6 | TB1 | TB2 | 38-42
|  | Spare |  |  | 0F | S2 | 4 | J2 | B2 | K7 | TB1 | TB2 | 44-48

## Status
| Update: | 2019-03-20 | [9 empty] | RTU Type: | CDC 44-550 with ASE Protocol Translator
Gore Junction 115kV Substation (PN)
Pt. | DNP TO EMS |  |  |  |  | CDC2 to RTU
Own | Type | Pt. | Point Description | kV | Function | Seq No. | STA Bit | Card Sw | Card Conn | Wall Pos | Term Strip | Term No. | Comments | Rev
| C & I | 0 | Fairview East 115 kV CB |  | OP/CL | 0 | 0/8 | S2 | J1 | C2 | TB-1 | 1-2
| C & I | 1 | Erie S.-Green Garden 115 kV CB |  | OP/CL | 0 | 1/9 | S2 | J1 | C2 | TB-1 | 4-5
| C & I | 2 | Relay Failure |  | NM/ALM | 0 | 2/10 | S2 | J1 | C2 | TB-1 | 6-7
| C & I | 3 | Carrier Failure |  | NM/ALM | 0 | 3/11 | S2 | J1 | C2 | TB-1 | 9-10
| C & I | 4 | Relay Communications Reset |  | NM/ALM | 0 | 4/12 | S2 | J1 | C2 | TB-1 | 11-12
| C & I | 5 | Spare |  |  | 0 | 5/13 | S2 | J1 | C2 | TB-1 | 14-15
| C & I | 6 | Spare |  |  | 0 | 6/14 | S2 | J1 | C2 | TB-1 | 16-17
| C & I | 7 | Spare |  |  | 0 | 7/15 | S2 | J1 | C2 | TB-1 | 19-20
| C & I | 8 | Spare |  |  | 1 | 0/8 | S1 | J1 | C2 | TB-2 | 1-2
| C & I | 9 | Spare |  |  | 1 | 1/9 | S1 | J1 | C2 | TB-2 | 4-5
| C & I | 10 | Spare |  |  | 1 | 2/10 | S1 | J1 | C2 | TB-2 | 6-7
| C & I | 11 | Spare |  |  | 1 | 3/11 | S1 | J1 | C2 | TB-2 | 9-10
| C & I | 12 | Spare |  |  | 1 | 4/12 | S1 | J1 | C2 | TB-2 | 11-12
| C & I | 13 | Spare |  |  | 1 | 5/13 | S1 | J1 | C2 | TB-2 | 14-15
| C & I | 14 | Spare |  |  | 1 | 6/14 | S1 | J1 | C2 | TB-2 | 16-17
| C & I | 15 | Spare |  |  | 1 | 7/15 | S1 | J1 | C2 | TB-2 | 19-20
| I | 16 | Local/Remote Switch - Status |  | LOC/REM | 30 | 0 | S4 | J2 | C1 | TB-1 | 1-2
| I | 17 | DC Over/Under Voltage |  | NM/ALM | 30 | 1 | S4 | J2 | C1 | TB-1 | 4-5
| I | 18 | Station Power |  | NM/ALM | 30 | 2 | S4 | J2 | C1 | TB-1 | 6-7
| I | 19 | DC System Ground Detect |  | NM/ALM | 30 | 3 | S4 | J2 | C1 | TB-1 | 9-10 | New pt | B
| I | 20 | Rolling Mead.Primary Relay Inop |  | NM/ALM | 30 | 4 | S4 | J2 | C1 | TB-1 | 11-12
| I | 21 | Rolling Mead.115 kV MOABS (Open) |  | CL/OP | 30 | 5 | S4 | J2 | C1 | TB-1 | 14-15
| I | 22 | Rolling Mead.115 kV MOABS(Close) |  | OP/CL | 30 | 6 | S4 | J2 | C1 | TB-1 | 16-17
| I | 23 | 115 kV CB Breaker Failure |  | NM/ALM | 30 | 7 | S4 | J2 | C1 | TB-1 | 19-20
| I | 24 | 115 Fairv.E Break Fail Cutoff Sw |  | OFF/ON | 30 | 8 | S3 | J2 | C1 | TB-2 | 1-2
| I | 25 | 115 ES-GG Breaker Fail Cutoff Sw |  | OFF/ON | 30 | 9 | S3 | J2 | C1 | TB-2 | 4-5
| I | 26 | Fair.East 115 kV CB Critical |  | NM/ALM | 30 | 10 | S3 | J2 | C1 | TB-2 | 6-7
| I | 27 | Fair.East 115 kV CB Non-Critical |  | NM/ALM | 30 | 11 | S3 | J2 | C1 | TB-2 | 9-10
| I | 28 | ES-GG 115 kV CB Critical |  | NM/ALM | 30 | 12 | S3 | J2 | C1 | TB-2 | 11-12
| I | 29 | ES-GG 115 kV CB Non-Critical |  | NM/ALM | 30 | 13 | S3 | J2 | C1 | TB-2 | 14-15
| I | 30 | 115 kV CB Low SF-6 Gas |  | NM/ALM | 30 | 14 | S3 | J2 | C1 | TB-2 | 16-17
| I | 31 | Trip Circuit Monitor |  | NM/ALM | 30 | 15 | S3 | J2 | C1 | TB-2 | 19-20
| I | 32 | SPT COMM FAIL |  | NM/ALM | SPT INTERNAL INDICATION | [6 empty] | New pt | A

## Analog
| Update: | 2019-03-20 | [10 empty] | RTU Type: | CDC 44-550 with ASE Protocol Translator
Gore Junction 115kV Substation (PN)
Pt. | DNP to EMS |  |  |  |  | CDC2 to RTU |  | Basket Card Analog Input Mux |  |  | Wall Card Analog Filter
Own | Type | Pt. | Point Description | kV | Function | Seq. | Scan | Card Sw | Card Loc | Panel | Wall Pos | Term Strip | CKT No. | Comments | Rev
| AI | 0 | Spare |  |  | 80 | [7 empty] | Spare "Full Scale" point upon project completion | A
| AI | 1 | Spare |  |  | 81 | [7 empty] | Spare "Zero Scale" point upon project completion | A
| AI | 2 | 115 kV Bus |  | V | 82 |  | S2 | 2 | J2 | A1 | TB1 | 1
| AI | 3 | Spare |  |  | 83 |  | S2 | 2 | J2 | A1 | TB1 | 2
| AI | 4 | Fairview East 115 kV |  | MW | 84 |  | S2 | 2 | J2 | A1 | TB1 | 3
| AI | 5 | Fairview East 115 kV |  | MVAR | 85 |  | S2 | 2 | J2 | A1 | TB1 | 4
| AI | 6 | Erie S.-Green Garden 115 kV |  | MW | 86 |  | S2 | 2 | J2 | A1 | TB2 | 5
| AI | 7 | Erie S.-Green Garden 115 kV |  | MVAR | 87 |  | S2 | 2 | J2 | A1 | TB2 | 6
| AI | 8 | Rolling Meadows 115 kV |  | MW | 88 |  | S2 | 2 | J2 | A1 | TB2 | 7
| AI | 9 | Rolling Meadows 115 kV |  | MVAR | 89 |  | S2 | 2 | J2 | A1 | TB2 | 8
| AI | 10 | Fairview E 115 Fault Distance |  | MILE | 8A |  | S1 | 2 | J1 | A2 | TB1 | 1
| AI | 11 | Erie S-GG 115 Fault Distance |  | MILE | 8B |  | S1 | 2 | J1 | A2 | TB1 | 2
| AI | 12 | Spare |  |  | 8C |  | S1 | 2 | J1 | A2 | TB1 | 3
| AI | 13 | Spare |  |  | 8D |  | S1 | 2 | J1 | A2 | TB1 | 4
| AI | 14 | Spare |  |  | 8E |  | S1 | 2 | J1 | A2 | TB2 | 5
| AI | 15 | Spare |  |  | 8F |  | S1 | 2 | J1 | A2 | TB2 | 6
| AI | 16 | Spare |  |  | 90 |  | S1 | 2 | J1 | A2 | TB2 | 7
| AI | 17 | Spare |  |  | 91 |  | S1 | 2 | J1 | A2 | TB2 | 8
Points in RTU not mapped to EMS
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)