## Revisions
Matawan (JC)
|  |  | Station Phone: |  | (732) 290-1102
|  |  | Latitude: |  | 40° 24’ 43”
EMS Information |  |  | Longitude: |  | 74° 13’ 34”
RTU Name: | MATAWAN | ASE SPT Physical Communication Ports
FEP: | RF5 | Communication
Channel: | 51 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10258 | Port 1: | DNP | 10258 | 10 | FE EAST EMS 9600 Baud | MPLS via 700MHz
|  | Port 2: | Not used
PLC Information |  | Port 3: | CDC2 | 30 | 4 | RTU, 1200 baud | RS232/Modem
Processor Type: | n/a | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | CDC 44-550 via ASE Protocol Translator
Size:
Powered At: |  |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-04-12 | Converted to Excel format. RTU being converted to DNP and cutover to MPLS via ASE Protocol Translator. Updated baud rate and FEP/CH (old FEP/CH MF2 C062). WO# 15730601; Scores 101162. Reviewed by H. Riley/BMcD | T. Menke (BMcD)
Address: | Lake Boulevard and First Street |  |  | B | 2019-11-05 | Added EMS Local Address. Created config for points list Rev A. Config: Matawan ASE SPT CDC2 DNP Rev A. WO# 15730601. | M. Smith (BMcD)
Aberdeen, NJ 07747

## Control
| Update: | 2019-11-05 | [6 empty] | RTU Type: | CDC 44-550 via ASE Protocol Translator
Matawan (JC)
DNP to EMS |  | RTU |  |  | CDC 2 to RTU |  | Device type | Card Slot | Control Inter-connection | Customer Termination
Type | Pt | Point Description | kV | Function | Seq No. | Relay No. |  |  |  |  | Comments | Rev
C | 0 | Z104-1 LBSW |  | CLOSE | 0 | K0C | CTRL | - | DO-1 | TB1-3,6
C |  | Z104-1 LBSW |  | OPEN | 0 | K0T | CTRL | - | DO-1 | TB2-3,6
C | 1 | Z104-2 LBSW |  | CLOSE | 1 | K1C | CTRL | - | DO-1 | TB1-9,12
C |  | Z104-2 LBSW |  | OPEN | 1 | K1T | CTRL | - | DO-1 | TB2-9,12
C | 2 | 43175 OCB |  | CLOSE | 2 | K2C | CTRL | - | DO-1 | TB1-15,18
C |  | 43175 OCB |  | OPEN | 2 | K2T | CTRL | - | DO-1 | TB2-15,18
C | 3 | 43176 OCB |  | CLOSE | 3 | K3C | CTRL | - | DO-1 | TB1-21,24
C |  | 43176 OCB |  | OPEN | 3 | K3T | CTRL | - | DO-1 | TB2-21,24
C | 4 | 43484 OCB |  | CLOSE | 4 | K4C | CTRL | - | DO-1 | TB1-27,30
C |  | 43484 OCB |  | OPEN | 4 | K4T | CTRL | - | DO-1 | TB2-27,30
C | 5 | UNDEFINED |  |  | Information missing from previous points list | [5 empty] | added to match EMS | A
C |  | UNDEFINED
C | 6 | UNDEFINED | [8 empty] | added to match EMS | A
C |  | UNDEFINED
C | 7 | UNDEFINED | [8 empty] | added to match EMS | A
C |  | UNDEFINED

## Status
| Update: | 2019-11-05 | [5 empty] | RTU Type: | CDC 44-550 via ASE Protocol Translator
DNP TO EMS |  |  |  |  | CDC to RTU |  | Card Slot | Interconne-ction | Customer Termination | Comments
Type | Pt. | Point Description | kV | Function | Add/Seq. No. | Mstr. Sta. Bit. |  |  |  |  | Rev
I | 0 | LOCAL/REMOTE |  | LOC/REM | 30 | 00 |  | DI-1 | TB1-1,2
I | 1 | BATTERY |  | NM/ALM | 30 | 01 |  | DI-1 | TB1-4,5
I | 2 | BK 1&2 OIL SPL |  | NM/ALM | 30 | 02 |  | DI-1 | TB1-6,7
I | 3 | Z104-1 LBSW | 34.5 | CL/OP | 30 | 03 |  | DI-1 | TB1-9,10
I | 4 | Z104-1 LBSW | 34.5 | OP/CL | 30 | 04 |  | DI-1 | TB1-11,22
I | 5 | Z104-2 LBSW | 34.5 | CL/OP | 30 | 05 |  | DI-1 | TB1-14,15
I | 6 | Z104-2 LBSW | 34.5 | OP/CL | 30 | 06 |  | DI-1 | TB1-16,17
I | 7 | TRIPPING DC |  | OFF/ON | 30 | 07 |  | DI-1 | TB1-19,20
I | 8 | SPARE |  |  | 30 | 08 |  | DI-1 | TB2-1,2
I | 9 | SPARE |  |  | 30 | 09 |  | DI-1 | TB2-4,5
I | 10 | SPARE |  |  | 30 | 10 |  | DI-1 | TB2-6,7
I | 11 | SPARE |  |  | 30 | 11 |  | DI-1 | TB2-9,10
I | 12 | SPARE |  |  | 30 | 12 |  | DI-1 | TB2-11,22
I | 13 | SPARE |  |  | 30 | 13 |  | DI-1 | TB2-14,15
I | 14 | SPARE |  |  | 30 | 14 |  | DI-1 | TB2-16,17
I | 15 | SPARE |  |  | 30 | 15 |  | DI-1 | TB2-19,20
I | 16 | 43175 OCB | 4.16 | OP/CL | 00 | 0,8 | - | D1-2 | TB1-1,2
I | 17 | 43176 OCB | 4.16 | OP/CL | 00 | 1,9 | - | D1-2 | TB1-4,5
I | 18 | 43484 OCB | 4.16 | OP/CL | 00 | 2,10 | - | D1-2 | TB1-6,7
I | 19 | SPARE |  |  | 00 | 3,11 | - | D1-2 | TB1-9,10
I | 20 | SPARE |  |  | 00 | 4,12 | - | D1-2 | TB1-11,12
I | 21 | SPARE |  |  | 00 | 5,13 | - | D1-2 | TB1-14,15
I | 22 | SPARE |  |  | 00 | 6,14 | - | D1-2 | TB1-16,17
I | 23 | SPARE |  |  | 00 | 7,15 | - | D1-2 | TB1-19,20
I | 24 | SPT COMM FAIL |  | NM/ALM |  | SPT INTERNAL INDICATION |  |  |  | New pt | A

## Analog
| Update: | 2019-11-05 | [8 empty] | RTU Type: | CDC 44-550 via ASE Protocol Translator
Matawan (JC)
Pt. | DNP to EMS |  |  | RTU | Device Type | CDC to RTU |  | Full | Card | Analog IO | Analog
Own | Type | Pt. | Point Description | kV |  | Add/Seq No | Scan Freq | Scale | Slot | Panel | Interconnection | Comments | Rev
| AI | 0 | SPARE |  | CNTS | 80 | [5 empty] | CDC II FULL SCALE Calibration, keep index spare. | A
| AI | 1 | SPARE |  | CNTS | 81 | [5 empty] | CDC II ZERO SCALE Calibration, keep index spare. | A
| AI | 2 | 43484 MW |  | MW | 82 |  |  | 2 | AI-1 | TB-1-1,2
| AI | 3 | 43484 MVAR |  | MX | 83 |  |  | 2 | AI-1 | TB-1-4,5
| AI | 4 | 43175 MW |  | MW | 84 |  |  | 2 | AI-1 | TB-1-7,8
| AI | 5 | 43175 MVAR |  | MX | 85 |  |  | 2 | AI-1 | TB-1-10,11
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)