## Revisions
HOOPER AVE (JC)
|  |  | Station Phone: |  | 732-349-5923
|  |  | Latitude: |  | 39° 59’ 19”
EMS Information |  |  | Longitude: |  | 74° 10’ 42”
RTU Name: | HOOPR_AV | ASE SPT Physical Communication Ports
FEP: | RF21 | Communication
Channel: | 77 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10243 | Port 1: | DNP | 10243 | 10 | FE East EMS 9600 Baud | Cellular IP, ON DEMAND
|  | Port 2: | TRWS9 | 20 | 1 | RTU, 2400 baud | RS232/Modem
PLC Information |  | Port 3: | Not used
Processor Type: | N/A | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | S-9000 via ASE Protocol Translator
Size:
Powered At: | 48 VDC |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-07-23 | Converted to Excel format. RTU being converted to DNP and cutover to Cellular IP via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF1 CH 32). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted. WO# 15627817 SCORES 105127. Reviewed by H. Riley/BMcD | J.McLaughlin (BMcD)
|  |  |  | B | 2019-10-04 | Removed redundant spaces from point descriptions on control and status sheets. Cleaned up the relay group numbers on the control sheet. Added status point device type on the status sheet according to EMS dump. Changed status point MCD points from "C&I" to just "I". | W. Blankenship (BMcD)

## Control
| Update: | 2019-07-23 | [6 empty] | RTU Type: | S-9000 via ASE Protocol Translator
HOOPER AVE (JC)
DNP to EMS |  |  |  |  | TRWS9 to RTU |  | Card Location |  | Customer
Type | Pt | Point Description | kV | Function | Relay Group | Relay | Cage | Slot | Termination | Comments | Rev
C | 0 | SPARE |  |  | 1 | 1 |  |  | None
C |  | SPARE |  |  | 1 | 2 |  |  | None
C | 1 | N92-1 LB |  | OP | 1 | 3 |  |  | 1A6-TB1 - 5,6
C |  | N92-1 LB |  | CL | 1 | 4 |  |  | 1A6-TB1 - 7,8
C | 2 | N92-2 LB |  | OP | 1 | 5 |  |  | 1A6-TB2 - 1,2
C |  | N92-2 LB |  | CL | 1 | 6 |  |  | 1A6-TB2 - 3,4 |  | B
C | 3 | NO. 6 LB |  | OP | 1 | 7 |  |  | 1A6-TB2 - 5,6
C |  | NO. 6 LB |  | CL | 1 | 8 |  |  | 1A6-TB2 - 7,8
C | 4 | BANK 1 ACB |  | OP | 1 | 9 |  |  | 1A6-TB3 - 1,2
C |  | BANK 1 ACB |  | CL | 1 | A |  |  | 1A6-TB3 - 3,4
C | 5 | 67260 LB |  | OP | 1 | B |  |  | 1A6-TB3 - 5,6
C |  | 67260 LB |  | CL | 1 | C |  |  | 1A6-TB3 - 7,8
C | 6 | 67261 LB |  | OP | 1 | D |  |  | 1A6-TB4 - 1,2
C |  | 67261 LB |  | CL | 1 | E |  |  | 1A6-TB4 - 3,4
C | 7 | CAP 1 VCB |  | OP | 1 | F |  |  | 1A6-TB4 - 5,6
C |  | CAP 1 VCB |  | CL | 1 | 10 |  |  | 1A6-TB4 - 7,8
C | 8 | BANK 2 VCB |  | OP | 2 | 1 |  |  | 2A6-TB1 - 1,2 |  | B
C |  | BANK 2 VCB |  | CL | 2 | 2 |  |  | 2A6-TB1 - 3,4
C | 9 | BUS TIE VCB |  | OP | 2 | 3 |  |  | 2A6-TB1 - 5,6
C |  | BUS TIE VCB |  | CL | 2 | 4 |  |  | 2A6-TB1 - 7,8
C | 10 | 67262 VCB |  | OP | 2 | 5 |  |  | 2A6-TB2 - 1,2
C |  | 67262 VCB |  | CL | 2 | 6 |  |  | 2A6-TB2 - 3,4
C | 11 | 67263 VCB |  | OP | 2 | 7 |  |  | 2A6-TB2 - 5,6
C |  | 67263 VCB |  | CL | 2 | 8 |  |  | 2A6-TB2 - 7,8
C | 12 | ADAPTIVE RELAYING |  | OFF | 2 | D |  |  | 2A6-TB4 - 1,2
C |  | ADAPTIVE RELAYING |  | ON | 2 | E |  |  | 2A6-TB4 - 3,4
C | 13 | 5% VOLT REDUCTION |  | OP | 2 | B |  |  | 2A6-TB3 - 5,6
C |  | 5% VOLT REDUCTION |  | CL | 2 | C |  |  | 2A6-TB3 - 7,8
C | 14 | SPARE |  | OP | 2 | 9 |  |  | 2A6-TB3 - 1,2
C |  | SPARE |  | CL | 2 | A |  |  | 2A6-TB3 - 3,4
C | 15 | SPARE |  |  | 2 | F |  |  | 2A6-TB4 - 5,6
C |  | SPARE |  |  | 2 | 10 |  |  | 2A6-TB4 - 7,8

## Status
| Update: | 2019-07-23 | [5 empty] | RTU Type: |  | S-9000 via ASE Protocol Translator
HOOPER AVE (JC)
Pt. | DNP to EMS |  |  |  |  | Device | TRWS9 to RTU |  |  | Card Location |  | Customer
Own | Type | Pt | Point Description | kV | Function | Type | FR | WD | Bit | Cage | Card Slot | Termination | Comments | Rev
| I | 0 | N92-1 LB “b” |  | OP | SS | 0 | 1 | 1 |  |  | 1A3-TB1 - 1 |  | B
| I | 1 | N92-1 LB “a” |  | CL | SS | 0 | 1 | 2 |  |  | 1A3-TB1 - 2 |  | B
| I | 2 | N92-2 LB “b” |  | OP | SS | 0 | 1 | 3 |  |  | 1A3-TB1 - 3 |  | B
| I | 3 | N92-2 LB “a” |  | CL | SS | 0 | 1 | 4 |  |  | 1A3-TB1 - 4 |  | B
| I | 4 | NO. 6 LB “b” |  | OP | SS | 0 | 1 | 5 |  |  | 1A3-TB1 - 5 |  | B
| I | 5 | NO. 6 LB “a” |  | CL | SS | 0 | 1 | 6 |  |  | 1A3-TB1 - 6 |  | B
| I | 6 | SPARE |  |  | SS | 0 | 1 | 7 |  |  | 1A3-TB1 - 7 |  | B
| I | 7 | BANK 2 ALARM |  | NM/ALM | SS | 0 | 1 | 8 |  |  | 1A3-TB1 - 8 |  | B
| I | 8 | BANK 1 ALARM |  | NM/ALM | SS | 0 | 1 | 9 |  |  | 1A3-TB1 - 9 |  | B
| I | 9 | STATION BATTERY |  | NM/ALM | SS | 0 | 1 | 10 |  |  | 1A3-TB1 - 10 |  | B
| I | 10 | LOCAL/REMOTE |  | LOC/REM | SS | 0 | 1 | 11 |  |  | 1A3-TB1 - 11 |  | B
| I | 11 | ADAPTIVE RELAYING |  | OFF/ON | SS | 0 | 1 | 12 |  |  | 1A3-TB1 - 12 |  | B
| I | 12 | VOLTAGE REDUCTION 5% |  | OFF/ON | SS | 0 | 1 | 13 |  |  | 1A3-TB1 - 13 |  | B
| I | 13 | CAP 1 VCB |  | OP/CL | SS | 0 | 1 | 14 |  |  | 1A3-TB1 - 14 |  | B
| I | 14 | SPARE |  |  | SS | 0 | 2 | 1 |  |  | 1A3-TB2 - 1 |  | B
| I | 15 | SPARE |  |  | SS | 0 | 2 | 2 |  |  | 1A3-TB2 - 2 |  | B
| I | 16 | SPARE |  |  | SS | 0 | 2 | 3 |  |  | 1A3-TB2 - 3 |  | B
| I | 17 | SPARE |  |  | SS | 0 | 2 | 4 |  |  | 1A3-TB2 - 4 |  | B
| I | 18 | SPARE |  |  | SS | 0 | 2 | 5 |  |  | 1A3-TB2 - 5 |  | B
| I | 19 | SPARE |  |  | SS | 0 | 2 | 6 |  |  | 1A3-TB2- 6 |  | B
| I | 20 | SPARE |  |  | SS | 0 | 2 | 7 |  |  | 1A3-TB2 - 7 |  | B
| I | 21 | SPARE |  |  | SS | 0 | 2 | 8 |  |  | 1A3-TB2 - 8 |  | B
| I | 22 | SPARE |  |  | SS | 0 | 2 | 9 |  |  | 1A3-TB2 - 9 |  | B
| I | 23 | SPARE |  |  | SS | 0 | 2 | 10 |  |  | 1A3-TB2 - 10 |  | B
| I | 24 | SPARE |  |  | SS | 0 | 2 | 11 |  |  | 1A3-TB2 - 11 |  | B
| I | 25 | SPARE |  |  | SS | 0 | 2 | 12 |  |  | 1A3-TB2 - 12 |  | B
| I | 26 | SPARE |  |  | SS | 0 | 2 | 13 |  |  | 1A3-TB2 - 13 |  | B
| I | 27 | SPARE |  |  | SS | 0 | 2 | 14 |  |  | 1A3-TB2 - 14 |  | B
| I | 28 | 67260 ACB |  | OP/CL | MCD | 0 | 3 | 1,2 |  |  | 1A3-TB4 - 1 |  | B
| I | 29 | 67261 ACB |  | OP/CL | MCD | 0 | 3 | 3,4 |  |  | 1A3-TB4 - 2 |  | B
| I | 30 | 67262 VCB |  | OP/CL | MCD | 0 | 3 | 5,6 |  |  | 1A3-TB4 - 3 |  | B
| I | 31 | BANK 1 ACB |  | OP/CL | MCD | 0 | 3 | 7,8 |  |  | 1A3-TB4- 4 |  | B
| I | 32 | BANK 2 VCB |  | OP/CL | MCD | 0 | 3 | 9,10 |  |  | 1A3-TB4 - 5 |  | B
| I | 33 | BUS TIE VCB |  | OP/CL | MCD | 0 | 3 | 11,12 |  |  | 1A3-TB4- 6 |  | B
| I | 34 | 67263 VCB |  | OP/CL | MCD | 0 | 3 | 13,14 |  |  | 1A3-TB4 - 7 |  | B
| I | 35 | SPARE |  |  | MCD | 0 | 4 | 1,2 |  |  | 1A3-TB5 – 1 |  | B
| I | 36 | SPARE |  |  | MCD | 0 | 4 | 3,4 |  |  | 1A3-TB5 – 2 |  | B
| I | 37 | SPARE |  |  | MCD | 0 | 4 | 5,6 |  |  | 1A3-TB5 - 3 |  | B
| I | 38 | SPARE |  |  | MCD | 0 | 4 | 7,8 |  |  | 1A3-TB5 – 4 |  | B
| I | 39 | SPARE |  |  | MCD | 0 | 4 | 9,10 |  |  | 1A3-TB5 - 5 |  | B
| I | 40 | SPARE |  |  | MCD | 0 | 4 | 11,12 |  |  | 1A3-TB5 - 6 |  | B
| I | 41 | SPARE |  |  | MCD | 0 | 4 | 13,14 |  |  | 1A3-TB5 - 7 |  | B
| I | 42 | SPT COMM FAIL |  | NM/ALM | [7 empty] | New point. | A

## Analog
| Update: | 2019-07-23 | [6 empty] | RTU Type: |  | S-9000 via ASE Protocol Translator
HOOPER AVE (JC)
Pt. | DNP to EMS |  |  | RTU | Device | TRWS9 to RTU |  | Scan | Card Location |  | I/O Panel |  |  | Customer
Own | Type | Pt. | Point Description | kV | Type | FR | WD | Freq. | Cage | Slot | +TB | -TB | S TB | Termination | Comments | Rev