## Revisions
Millhurst (JC)
|  |  | Station Phone: |  | 732-462-3861
|  |  | Latitude: |  | 40° 15’ 15”
EMS Information |  |  | Longitude: |  | 74° 20’ 29”
RTU Name: | MILLHRST | ASE SPT Physical Communication Ports
FEP: | RF0 | Communication
Channel: | 60 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10237 | Port 1: | DNP | 10237 | 10 | FE East EMS 9600 Baud | Cellular Serial
|  | Port 2: | TRWS9 | 20 | 3 | RTU, 1200 baud | RS232/Modem
PLC Information |  | Port 3: | Not used
Processor Type: | N/A | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | S-9000 via ASE Protocol Translator
Size:
Powered At: | 48 VDC |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-06-07 | Converted to Excel format. RTU being converted to DNP and cutover to Cellular Serial via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF1 CH 25). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted in red. WO# 16049090, SCORES ID 104377. Reviewed by J.McLaughlin (BMcD); H. Riley/BMcD | J.McLaughlin (BMcD)
|  |  |  | B | 7/3//2019 | Revision built upon points list rev A. Updated status points 0-13 to type I from C&I. W.Blankenship(BMcD) | W.Blankenship(BMcD)

## Control
| Update: | 2019-06-07 | [7 empty] | RTU Type: | S-9000 via ASE Protocol Translator
Millhurst (JC)
DNP to EMS |  |  |  |  | TRWS9 to RTU |  | Card Location |  | Relay | Customer
Type | Pt | Point Description | kV | Function | Relay Group | Relay | Cage | Slot | Interface | Termination | Comments | Rev
C | 0 | DIAL IN ACCESS |  | ENABLE | 1 | 1 | 1A1 | 5 | 2A5-TB1-1,2 | 2A6-TB1-1,2 |  | A
C |  | DIAL IN ACCESS |  | DISABLE | 1 | 2 | 1A1 | 5 | 2A5-TB1-3,4 | 2A6-TB1-3,4 |  | A
C | 1 | I87 LBSW |  | OPEN | 1 | 3 | 1A1 | 5 | 2A5-TB1-5,6 | 2A6-TB1-5,6 |  | A
C |  | I87 LBSW |  | CLOSE | 1 | 4 | 1A1 | 5 | 2A5-TB1-7,8 | 2A6-TB1-7,8 |  | A
C | 2 | NO 6 LBSW |  | OPEN | 1 | 5 | 1A1 | 5 | 2A5-TB1-9,10 | 2A6-TB2-1,2 |  | A
C |  | NO 6 LBSW |  | CLOSE | 1 | 6 | 1A1 | 5 | 2A5-TB1-11,12 | 2A6-TB2-3,4 |  | A
C | 3 | A53 LBSW |  | OPEN | 1 | 7 | 1A1 | 5 | 2A5-TB1-13,14 | 2A6-TB2-5,6 |  | A
C |  | A53 LBSW |  | CLOSE | 1 | 8 | 1A1 | 5 | 2A5-TB1-15,16 | 2A6-TB2-7,8 |  | A
C | 4 | BK 1 VCB |  | OPEN | 1 | 9 | 1A1 | 5 | 2A5-TB2-1,2 | 2A6-TB3-1,2 |  | A
C |  | BK 1 VCB |  | CLOSE | 1 | 10 | 1A1 | 5 | 2A5-TB2-3,4 | 2A6-TB3-3,4 |  | A
C | 5 | 47417 VCB |  | OPEN | 1 | 11 | 1A1 | 5 | 2A5-TB2-5,6 | 2A6-TB3-5,6 |  | A
C |  | 47417 VCB |  | CLOSE | 1 | 12 | 1A1 | 5 | 2A5-TB2-7,8 | 2A6-TB3-7,8 |  | A
C | 6 | BT VCB |  | OPEN | 1 | 13 | 1A1 | 5 | 2A5-TB2-9,10 | 2A6-TB4-1,2 |  | A
C |  | BT VCB |  | CLOSE | 1 | 14 | 1A1 | 5 | 2A5-TB2-11,12 | 2A6-TB4-3,4 |  | A
C | 7 | BK 2 VCB |  | OPEN | 1 | 15 | 1A1 | 5 | 2A5-TB2-13,14 | 2A6-TB4-5,6 |  | A
C |  | BK 2 VCB |  | CLOSE | 1 | 16 | 1A1 | 5 | 2A5-TB2-15,16 | 2A6-TB4-7,8 |  | A
C | 8 | 47418 VCB |  | OPEN | 2 | 1 | 1A1 | 5 | 2A5-TB3-1,2 | 2A7-TB1-1,2 |  | A
C |  | 47418 VCB |  | CLOSE | 2 | 2 | 1A1 | 5 | 2A5-TB3-3,4 | 2A7-TB1-3,4 |  | A
C | 9 | 47419 VCB |  | OPEN | 2 | 3 | 1A1 | 5 | 2A5-TB3-5,6 | 2A7-TB1-5,6 |  | A
C |  | 47419 VCB |  | CLOSE | 2 | 4 | 1A1 | 5 | 2A5-TB3-7,8 | 2A7-TB1-7,8 |  | A
C | 10 | 47416 VCB |  | OPEN | 2 | 5 | 1A1 | 5 | 2A5-TB3-9,10 | 2A7-TB2-1,2 |  | A
C |  | 47416 VCB |  | CLOSE | 2 | 6 | 1A1 | 5 | 2A5-TB3-11,12 | 2A7-TB2-3,4 |  | A
C | 11 | CAP 1 VCB |  | OPEN | 2 | 7 | 1A1 | 5 | 2A5-TB3-13,14 | 2A7-TB2-5,6 |  | A
C |  | CAP 1 VCB |  | CLOSE | 2 | 8 | 1A1 | 5 | 2A5-TB3-15,16 | 2A7-TB2-7,8 |  | A
C | 12 | 47415 VCB |  | OPEN | 2 | 9 | 1A1 | 5 | 2A5-TB3-1,2 | 2A7-TB3-1,2 |  | A
C |  | 47415 VCB |  | CLOSE | 2 | 10 | 1A1 | 5 | 2A5-TB3-3,4 | 2A7-TB3-3,4 |  | A
C | 13 | BK 1 CKT INT CI-2 |  | OPEN | 2 | 11 |  |  |  | TBA-27 |  | A
C |  | BK 1 CKT INT CI-2 |  | CLOSE | 2 | 12 |  |  |  | TBA-28 |  | A
C | 14 | ADAPTIVE RELAYINIG |  | OFF | 2 | 13 | 1A1 | 5 | 2A5-TB3-5,6 | 2A7-TB3-5,6 |  | A
C |  | ADAPTIVE RELAYINIG |  | ON | 2 | 14 | 1A1 | 5 | 2A5-TB3-7,8 | 2A7-TB3-7,8 |  | A
C | 15 | UNDEFINED | INFORMATION MISSING FROM ORIGINAL PT LIST | [7 empty] | Updated to match EMS | A
C |  | UNDEFINED | [8 empty] | Updated to match EMS | A

## Status
| Update: | 2019-06-07 | [5 empty] | RTU Type: |  | S-9000 via ASE Protocol Translator
Millhurst (JC)
Pt. | DNP to EMS |  |  |  |  | Type | TRWS9 to RTU |  |  | Card Location |  | I/O Panel |  | Customer
Own | Type | Pt | Point Description | kV | Function |  | FR | WD | Bit | Cage | Card Slot | Input TB | +24 VDC TB | Termination | Comments | Rev
| I | 0 | BK 1 VCB |  | OP/CL | CD | 0 | 1 | 1,2 | 1A1 | 11 | 5-1 | 5-2 | WIRE DIRECT TO 1A6 |  | A
| I | 1 | 47417 VCB |  | OP/CL | CD | 0 | 1 | 3,4 | 1A1 | 11 | 5-3 | 5-4 | WIRE DIRECT TO 1A6 |  | A
| I | 2 | BT VCB |  | OP/CL | CD | 0 | 1 | 5,6 | 1A1 | 11 | 5-5 | 5-6 | WIRE DIRECT TO 1A6 |  | A
| I | 3 | BK 2 VCB |  | OP/CL | CD | 0 | 1 | 7,8 | 1A1 | 11 | 5-7 | 5-8 | WIRE DIRECT TO 1A6 |  | A
| I | 4 | 47418 VCB |  | OP/CL | CD | 0 | 1 | 9,10 | 1A1 | 11 | 5-9 | 5-10 | WIRE DIRECT TO 1A6 |  | A
| I | 5 | 47419 VCB |  | OP/CL | CD | 0 | 1 | 11,12 | 1A1 | 11 | 5-11 | 5-12 | WIRE DIRECT TO 1A6 |  | A
| I | 6 | 47416 VCB |  | OP/CL | CD | 0 | 1 | 13,14 | 1A1 | 11 | 5-13 | 5-14 | WIRE DIRECT TO 1A6 |  | A
| I | 7 | 47415 VCB |  | OP/CL | CD | 0 | 1 | 15,16 | 1A1 | 11 | 5-15 | 5-16 | WIRE DIRECT TO 1A6 |  | A
| I | 8 | DIAL IN ACCESS |  | DIS/EN | CD | 0 | 2 | 1,2 | 1A1 | 12 | 6-1 | 6-2 | WIRE DIRECT TO 1A6 | Field to verify | A | Original points list was out of order in this region.
| I | 9 | BK 1 CKT INT CI-2 |  | OP/CL | CD | 0 | 2 | 3,4 | 1A1 | 12 | 6-3 | 6-4 | WIRE DIRECT TO 1A6 | Field to verify | A
| I | 10 | SPARE |  |  | CD | 0 | 2 | 5,6 | 1A1 | 12 | 6-5 | 6-6 | TBD19, 20 | Field to verify | A
| I | 11 | SPARE |  |  | CD | 0 | 2 | 7,8 | 1A1 | 12 | 6-7 | 6-8 | WIRE DIRECT TO 1A6 | Field to verify | A
| I | 12 | SPARE |  |  | CD | 0 | 2 | 9,10 | 1A1 | 12 | 6-9 | 6-10 | WIRE DIRECT TO 1A6 | Field to verify | A
| I | 13 | SPARE |  |  | CD | 0 | 2 | 11,12 | 1A1 | 12 | 6-11 | 6-12 | WIRE DIRECT TO 1A6 | Field to verify | A
| I | 14 | I87 LBSW |  | CL/OP | NL | 0 | 3 | 1 | 1A1 | 13 | 7-1 | 7-2 | WIRE DIRECT TO 1A6 |  | A
| I | 15 | I87 LBSW |  | OP/CL | NL | 0 | 3 | 2 | 1A1 | 13 | 7-3 | 7-4 | WIRE DIRECT TO 1A6 |  | A
| I | 16 | NO 6 LBSW |  | CL/OP | NL | 0 | 3 | 3 | 1A1 | 13 | 7-5 | 7-6 | WIRE DIRECT TO 1A6 |  | A
| I | 17 | NO 6 LBSW |  | OP/CL | NL | 0 | 3 | 4 | 1A1 | 13 | 7-7 | 7-8 | WIRE DIRECT TO 1A6 |  | A
| I | 18 | A53 LBSW |  | CL/OP | NL | 0 | 3 | 5 | 1A1 | 13 | 7-9 | 7-10 | WIRE DIRECT TO 1A6 |  | A
| I | 19 | A53 LBSW |  | OP/CL | NL | 0 | 3 | 6 | 1A1 | 13 | 7-11 | 7-12 | WIRE DIRECT TO 1A6 |  | A
| I | 20 | BK 1 ALRM |  | NM/ALM | NL | 0 | 3 | 7 | 1A1 | 13 | 7-13 | 7-14 | WIRE DIRECT TO 1A6 |  | A
| I | 21 | BK 2 ALRM |  | NM/ALM | NL | 0 | 3 | 8 | 1A1 | 13 | 7-15 | 7-16 | WIRE DIRECT TO 1A6 |  | A
| I | 22 | CAP 1 VCB |  | CAP | NL | 0 | 3 | 9 | 1A1 | 14 | 8-1 | 8-2 | WIRE DIRECT TO 1A6 |  | A
| I | 23 | DX RELAY FAIL |  | NM/ALM | NL | 0 | 3 | 10 | 1A1 | 14 | 8-3 | 8-4 | WIRE DIRECT TO 1A6 |  | A
| I | 24 | LOSS OF POTENTIAL |  | NM/ALM | NL | 0 | 3 | 11 | 1A1 | 14 | 8-5 | 8-6 | TBD21, 22 |  | A
| I | 25 | BK 1 CKT INT CI-2/SEL TRBL |  | NM/ALM | NL | 0 | 3 | 12 | 1A1 | 14 | 8-7 | 8-8 | TBD-7,8 |  | A
| I | 26 | ADAPTIVE RELAYING |  | OFF/ON | NL | 0 | 3 | 13 | 1A1 | 14 | 8-9 | 8-10 | WIRE DIRECT TO 1A6 |  | A
| I | 27 | LOCAL/REMOTE |  | LOC/REM | NL | 0 | 3 | 14 | 1A1 | 14 | 8-11 | 8-12 | WIRE DIRECT TO 1A6 |  | A
| I | 28 | UNDEFINED | INFORMATION MISSING FROM ORIGINAL PT LIST | [10 empty] | Updated to match EMS | A
| I | 29 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 30 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 31 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 32 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 33 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 34 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 35 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 36 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 37 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 38 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 39 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 40 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 41 | UNDEFINED | [11 empty] | Updated to match EMS | A
| I | 42 | SPT COMM FAIL |  | NM/ALM | SPT INTERNAL INDICATION | [8 empty] | New point. | A

## Analog
| Update: | 2019-06-07 | [6 empty] | RTU Type: |  | S-9000 via ASE Protocol Translator
Millhurst (JC)
Pt. | DNP to EMS |  |  | RTU | Device | TRWS9 to RTU |  | Scan | Card Location |  | I/O Panel |  |  | Customer
Own | Type | Pt. | Point Description | kV | Type | FR | WD | Freq. | Cage | Slot | +TB | -TB | S TB | Termination | Comments | Rev
| AI | 0 | SPARE |  | CNTS | 0 | 1 | 30 | 1A1 | 9 | 2-1 | 2-2 |  |  | Spare 90PCT A/D CAL, keep index spare. | A
| AI | 1 | SPARE |  | CNTS | 0 | 2 | 30 | 1A1 | 9 | 2-3 | 2-4 |  |  | Spare 10PCT A/D CAL, keep index spare. | A
| AI | 2 | BK 1 MW |  | MW | 0 | 3 | 30 | 1A1 | 9 | 2-5 | 2-6 |  |  |  | A
| AI | 3 | BK 1 MVAR |  | MX | 0 | 4 | 30 | 1A1 | 9 | 2-7 | 2-8 |  |  |  | A
| AI | 4 | BK 2 MW |  | MW | 1 | 1 | 30 | 1A1 | 9 | 2-9 | 2-10 |  |  |  | A
| AI | 5 | BK 2 MVAR |  | MX | 1 | 2 | 30 | 1A1 | 9 | 2-11 | 2-12 |  |  |  | A
| AI | 6 | 47416 phase A amps | 1200 | A | 1 | 3 | 30 | 1A1 | 9 | 2-13 | 2-14 |  | TB2 13, 14 |  | A
| AI | 7 | 47416 phase B amps | 1200 | A | 1 | 4 | 30 | 1A1 | 9 | 2-15 | 2-16 |  | TB2 15, 16 |  | A
| AI | 8 | 47416 phase C amps | 600 | A | 2 | 1 | 31 | 1A1 | 10 | 4-1 | 4-2 |  | TB4 1, 2 |  | A
| AI | 9 | 47417 phase A amps | 1200 | A | 2 | 2 | 31 | 1A1 | 10 | 4-3 | 4-4 |  | TB4 3,4 |  | A
| AI | 10 | 47417 phase B amps | 1200 | A | 2 | 3 | 31 | 1A1 | 10 | 4-5 | 4-6 |  | TB4 5, 6 |  | A
| AI | 11 | 47417 phase C amps | 600 | A | 2 | 4 | 31 | 1A1 | 10 | 4-7 | 4-8 |  | TB4 7, 8 |  | A
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)