## Revisions
TOMS RIVER (JC)
|  |  | Station Phone: |  | 732-854-0861
|  |  | Latitude: |  | N39° 57' 14''
EMS Information |  |  | Longitude: |  | W74° 12' 18''
RTU Name: | TOMS_RVR | ASE SPT Physical Communication Ports
FEP: | RF21 | Communication
Channel: | 79 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10250 | Port 1: | DNP | 10250 | 10 | FE East EMS 9600 Baud | Cellular IP
|  | Port 2: | TRWS9 | 20 | 3 | RTU, 2400 baud | RS232/Modem
PLC Information |  | Port 3: | Not used
Processor Type: | N/A | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | S-9000 via ASE Protocol Translator
Size:
Powered At: |  |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-08-05 | RTU being converted to DNP and cutover to Cellular IP via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF1 CH 26). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted. WO# 16063652 SCORES 105140. Reviewed by H.Riley/BMcD | J.McLaughlin (BMcD)
|  |  |  | B | 2019-11-11 | Added Type to status points on the Status sheet. Also, updated DNP type to EMS from C&I to just I to represent point functions correctly. | W.Blankenship (BMcD)

## Control
| Update: | 2019-08-05 | [10 empty] | RTU Type: |  | S-9000 via ASE Protocol Translator
TOMS RIVER (JC)
DNP to EMS |  |  |  |  | TRWS9 to RTU |  | Card Location |  | Relay Interface |  |  | Customer
Type | Pt | Point Description | kV | Function | GRP | RLY | Cage | Slot | PNL | TB | Term | PNL | TB | Term | Comments | Rev
C | 0 | "DO NOT USE" |  | OPEN | 1 | 1 | A1 | A5 | A3 | 1 | 1/2
C |  |  |  | CLOSE | 1 | 2 | A1 | A5 | A3 | 1 | 5/6
C | 1 | D212 LBSW |  | OPEN | 1 | 3 | A1 | A5 | A3 | 1 | 9/10
C |  |  |  | CLOSE | 1 | 4 | A1 | A5 | A3 | 1 | 13/14
C | 2 | NO. 6 LBSW |  | OPEN | 1 | 5 | A1 | A5 | A3 | 2 | 1/2
C |  |  |  | CLOSE | 1 | 6 | A1 | A5 | A3 | 2 | 5/6
C | 3 | V126 LBSW |  | OPEN | 1 | 7 | A1 | A5 | A3 | 2 | 9/10
C |  |  |  | CLOSE | 1 | 8 | A1 | A5 | A3 | 2 | 13/14
C | 4 | ADAPTIVE RELAYING |  | OFF | 1 | 9 | A1 | A5 | A3 | 3 | 1/2
C |  |  |  | ON | 1 | 10 | A1 | A5 | A3 | 3 | 5/6
C | 5 | BANK 1 ACB |  | OPEN | 1 | 11 | A1 | A5 | A3 | 3 | 9/10
C |  |  |  | CLOSE | 1 | 12 | A1 | A5 | A3 | 3 | 13/14
C | 6 | BANK 2 ACB |  | OPEN | 1 | 13 | A1 | A5 | A3 | 4 | 1/2
C |  |  |  | CLOSE | 1 | 14 | A1 | A5 | A3 | 4 | 5/6
C | 7 | BT ACB |  | OPEN | 1 | 15 | A1 | A5 | A3 | 4 | 9/10
C |  |  |  | CLOSE | 1 | 16 | A1 | A5 | A3 | 4 | 13/14
C | 8 | 64026 ACB |  | OPEN | 2 | 1 | A1 | A5 | A4 | 1 | 1/2
C |  |  |  | CLOSE | 2 | 2 | A1 | A5 | A4 | 1 | 5/6
C | 9 | 64023 ACB |  | OPEN | 2 | 3 | A1 | A5 | A4 | 1 | 9/10
C |  |  |  | CLOSE | 2 | 4 | A1 | A5 | A4 | 1 | 13/14
C | 10 | 64025 ACB |  | OPEN | 2 | 5 | A1 | A5 | A4 | 2 | 1/2
C |  |  |  | CLOSE | 2 | 6 | A1 | A5 | A4 | 2 | 5/6
C | 11 | 64028 ACB |  | OPEN | 2 | 7 | A1 | A5 | A4 | 2 | 9/10
C |  |  |  | CLOSE | 2 | 8 | A1 | A5 | A4 | 2 | 13/14
C | 12 | 64021 ACB |  | OPEN | 2 | 9 | A1 | A5 | A4 | 3 | 1/2
C |  |  |  | CLOSE | 2 | 10 | A1 | A5 | A4 | 3 | 5/6
C | 13 | 64024 ACB |  | OPEN | 2 | 11 | A1 | A5 | A4 | 3 | 9/10
C |  |  |  | CLOSE | 2 | 12 | A1 | A5 | A4 | 3 | 13/14
C | 14 | 64022 ACB |  | OPEN | 2 | 13 | A1 | A5 | A4 | 4 | 1/2
C |  |  |  | CLOSE | 2 | 14 | A1 | A5 | A4 | 4 | 5/6
C | 15 | SPARE BREAKER |  | OPEN | 2 | 15 | A1 | A5 | A4 | 4 | 9/10
C |  |  |  | CLOSE | 2 | 16 | A1 | A5 | A4 | 4 | 13/14
C | 16 | SPARE BREAKER |  | OPEN | 3 | 1 | A1 | A5 | A3 | 1 | 1/2
C |  |  |  | CLOSE | 3 | 2 | A1 | A5 | A3 | 1 | 5/6
C | 17 | SPARE |  |  | 3 | 3 | A1 | A5 | A3 | 1 | 9/10
C |  |  |  |  | 3 | 4 | A1 | A5 | A3 | 1 | 13/14
C | 18 | SPARE |  |  | 3 | 5 | A1 | A5 | A3 | 2 | 1/2
C |  |  |  |  | 3 | 6 | A1 | A5 | A3 | 2 | 5/6
C | 19 | UNDEFINED |  |  | 3 | 7 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C |  |  |  |  | 3 | 8 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C | 20 | UNDEFINED |  |  | 3 | 9 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C |  |  |  |  | 3 | 10 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C | 21 | UNDEFINED |  |  | 3 | 11 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C |  |  |  |  | 3 | 12 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C | 22 | UNDEFINED |  |  | 3 | 13 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C |  |  |  |  | 3 | 14 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C | 23 | UNDEFINED |  |  | 3 | 15 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
C |  |  |  |  | 3 | 16 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.

## Status
| Update: | 2019-08-05 | [5 empty] | RTU Type: |  | S-9000 via ASE Protocol Translator
TOMS RIVER (JC)
Pt. | DNP to EMS | [5 empty] | TRWS9 to RTU |  |  | Card Location |  | I/O Panel |  |  | Customer
Own | Type | Pt | Point Description | kV | Function | Type | FR | WD | Bit | Cage | Card Slot | Pnl | Input | -24 Vdc | Pnl | TB | Term | Comments | Rev
| I | 0 | D212 LBSW |  | OPEN | SS | 0 | 1 | 1 | B1 | A7 | B3 | 1-1 | 1-2
| I | 1 | D212 LBSW |  | CLOSE | SS | 0 | 1 | 2 | B1 | A7 | B3 | 1-3 | 1-4
| I | 2 | NO. 6 LBSW |  | OPEN | SS | 0 | 1 | 3 | B1 | A7 | B3 | 1-5 | 1-6
| I | 3 | NO. 6 LBSW |  | CLOSE | SS | 0 | 1 | 4 | B1 | A7 | B3 | 1-7 | 1-8
| I | 4 | V126 LBSW |  | OPEN | SS | 0 | 1 | 5 | B1 | A7 | B3 | 1-9 | 1-10
| I | 5 | V126 LBSW |  | CLOSE | SS | 0 | 1 | 6 | B1 | A7 | B3 | 1-11 | 1-12
| I | 6 | ADAPTIVE RELAYING |  | OFF/ON | SS | 0 | 1 | 7 | B1 | A7 | B3 | 1-13 | 1-14
| I | 7 | SPARE |  |  | SS | 0 | 1 | 8 | B1 | A8 | B3 | 2-1 | 2-2
| I | 8 | SPARE |  |  | SS | 0 | 1 | 9 | B1 | A8 | B3 | 2-3 | 2-4
| I | 9 | SPARE |  |  | SS | 0 | 1 | 10 | B1 | A8 | B3 | 2-5 | 2-6
| I | 10 | SPARE |  |  | SS | 0 | 1 | 11 | B1 | A8 | B3 | 2-7 | 2-8
| I | 11 | SPARE BREAKER |  | OP/CL | SS | 0 | 1 | 12 | B1 | A8 | B3 | 2-9 | 2-10
| I | 12 | SPARE BREAKER |  | OP/CL | SS | 0 | 1 | 13 | B1 | A8 | B3 | 2-11 | 2-12
| I | 13 | SPARE |  |  | SS | 0 | 1 | 14 | B1 | A8 | B3 | 2-13 | 2-14
| I | 14 | SPARE |  |  | SS | 0 | 2 | 1 | B1 | A9 | B3 | 3-1 | 3-2
| I | 15 | SPARE |  |  | SS | 0 | 2 | 2 | B1 | A9 | B3 | 3-3 | 3-4
| I | 16 | SPARE |  |  | SS | 0 | 2 | 3 | B1 | A9 | B3 | 3-5 | 3-6
| I | 17 | SPARE |  |  | SS | 0 | 2 | 4 | B1 | A9 | B3 | 3-7 | 3-8
| I | 18 | SPARE |  |  | SS | 0 | 2 | 5 | B1 | A9 | B3 | 3-9 | 3-10
| I | 19 | SPARE |  |  | SS | 0 | 2 | 6 | B1 | A9 | B3 | 3-11 | 3-12
| I | 20 | SPARE |  |  | SS | 0 | 2 | 7 | B1 | A9 | B3 | 3-13 | 3-14
| I | 21 | SPARE |  |  | SS | 0 | 2 | 8 | B1 | A10 | B3 | 4-1 | 4-2
| I | 22 | SPARE |  |  | SS | 0 | 2 | 9 | B1 | A10 | B3 | 4-3 | 4-4
| I | 23 | SPARE |  |  | SS | 0 | 2 | 10 | B1 | A10 | B3 | 4-5 | 4-6
| I | 24 | SPARE |  |  | SS | 0 | 2 | 11 | B1 | A10 | B3 | 4-7 | 4-8
| I | 25 | SPARE |  |  | SS | 0 | 2 | 12 | B1 | A10 | B3 | 4-9 | 4-10
| I | 26 | SPARE |  |  | SS | 0 | 2 | 13 | B1 | A10 | B3 | 4-11 | 4-12
| I | 27 | SPARE |  |  | SS | 0 | 2 | 14 | B1 | A10 | B3 | 4-13 | 4-14
| I | 28 | SPARE |  |  | SS | 0 | 3 | 1 | B1 | A11 | B3 | 1-1 | 1-2
| I | 29 | SPARE |  |  | SS | 0 | 3 | 2 | B1 | A11 | B3 | 1-3 | 1-4
| I | 30 | SPARE |  |  | SS | 0 | 3 | 3 | B1 | A11 | B3 | 1-5 | 1-6
| I | 31 | GSA ALARM |  | NM/ALM | SS | 0 | 3 | 4 | B1 | A11 | B3 | 1-7 | 1-8
| I | 32 | STATION BATTERY LOW |  | NM/ALM | SS | 0 | 3 | 5 | B1 | A11 | B3 | 1-9 | 1-10
| I | 33 | LOCAL REMOTE SWITCH STATUS |  | LOC/REM | SS | 0 | 3 | 6 | B1 | A11 | B3 | 1-11 | 1-12
| I | 34 | SPARE |  |  | SS | 0 | 3 | 7 | B1 | A11 | B3 | 1-13 | 1-14
| I | 35 | SPARE |  |  | SS | 0 | 3 | 8 | B1 | A12 | B3 | 2-1 | 2-2
| I | 36 | SPARE |  |  | SS | 0 | 3 | 9 | B1 | A12 | B3 | 2-3 | 2-4
| I | 37 | SPARE |  |  | SS | 0 | 3 | 10 | B1 | A12 | B3 | 2-5 | 2-6
| I | 38 | SPARE |  |  | SS | 0 | 3 | 11 | B1 | A12 | B3 | 2-7 | 2-8
| I | 39 | SPARE |  |  | SS | 0 | 3 | 12 | B1 | A12 | B3 | 2-9 | 2-10
| I | 40 | SPARE |  |  | SS | 0 | 3 | 13 | B1 | A12 | B3 | 2-11 | 2-12
| I | 41 | SPARE |  |  | SS | 0 | 3 | 14 | B1 | A12 | B3 | 2-13 | 2-14
| I | 42 | SPARE |  |  | SS | 0 | 4 | 1 | B1 | A13 | B3 | 3-1 | 3-2
| I | 43 | SPARE |  |  | SS | 0 | 4 | 2 | B1 | A13 | B3 | 3-3 | 3-4
| I | 44 | SPARE |  |  | SS | 0 | 4 | 3 | B1 | A13 | B3 | 3-5 | 3-6
| I | 45 | SPARE |  |  | SS | 0 | 4 | 4 | B1 | A13 | B3 | 3-7 | 3-8
| I | 46 | SPARE |  |  | SS | 0 | 4 | 5 | B1 | A13 | B3 | 3-9 | 3-10
| I | 47 | SPARE |  |  | SS | 0 | 4 | 6 | B1 | A13 | B3 | 3-11 | 3-12
| I | 48 | SPARE |  |  | SS | 0 | 4 | 7 | B1 | A13 | B3 | 3-13 | 3-14
| I | 49 | SPARE |  |  | SS | 0 | 4 | 8 | B1 | A14 | B3 | 4-1 | 4-2
| I | 50 | SPARE |  |  | SS | 0 | 4 | 9 | B1 | A14 | B3 | 4-3 | 4-4
| I | 51 | SPARE |  |  | SS | 0 | 4 | 10 | B1 | A14 | B3 | 4-5 | 4-6
| I | 52 | SPARE |  |  | SS | 0 | 4 | 11 | B1 | A14 | B3 | 4-7 | 4-8
| I | 53 | SPARE |  |  | SS | 0 | 4 | 12 | B1 | A14 | B3 | 4-9 | 4-10
| I | 54 | SPARE |  |  | SS | 0 | 4 | 13 | B1 | A14 | B3 | 4-11 | 4-12
| I | 55 | SPARE |  |  | SS | 0 | 4 | 14 | B1 | A14 | B3 | 4-13 | 4-14
| I | 56 | 64026 ACB |  | OP/CL | MCD | 1 | 1 | 1,2 | A1 | A11 | A2 | 5-1 | 5-2
| I | 57 | 64023 ACB |  | OP/CL | MCD | 1 | 1 | 3,4 | A1 | A11 | A2 | 5-3 | 5-4
| I | 58 | 64025 ACB |  | OP/CL | MCD | 1 | 1 | 5,6 | A1 | A11 | A2 | 5-5 | 5-6
| I | 59 | 64028 ACB |  | OP/CL | MCD | 1 | 1 | 7,8 | A1 | A11 | A2 | 5-7 | 5-8
| I | 60 | 64021 ACB |  | OP/CL | MCD | 1 | 1 | 9,10 | A1 | A11 | A2 | 5-9 | 5-10
| I | 61 | 64024 ACB |  | OP/CL | MCD | 1 | 1 | 11,12 | A1 | A11 | A2 | 5-11 | 5-12
| I | 62 | 64022 ACB |  | OP/CL | MCD | 1 | 1 | 13,14 | A1 | A11 | A2 | 5-13 | 5-14
| I | 63 | BANK 1 ACB |  | OP/CL | MCD | 1 | 2 | 1,2 | A1 | A12 | A2 | 6-1 | 6-2
| I | 64 | BANK 2 ACB |  | OP/CL | MCD | 1 | 2 | 3,4 | A1 | A12 | A2 | 6-3 | 6-4
| I | 65 | BT ACB |  | OP/CL | MCD | 1 | 2 | 5,6 | A1 | A12 | A2 | 6-5 | 6-6
| I | 66 | SPARE |  |  | MCD | 1 | 2 | 7,8 | A1 | A12 | A2 | 6-7 | 6-8
| I | 67 | SPARE |  |  | MCD | 1 | 2 | 9,10 | A1 | A12 | A2 | 6-9 | 6-10
| I | 68 | SPARE |  |  | MCD | 1 | 2 | 11,12 | A1 | A12 | A2 | 6-11 | 6-12
| I | 69 | SPARE |  |  | MCD | 1 | 2 | 13,14 | A1 | A12 | A2 | 6-13 | 6-14
| I | 70 | UNDEFINED |  |  | MCD | 1 | 3 | 1,2 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 71 | UNDEFINED |  |  | MCD | 1 | 3 | 3,4 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 72 | UNDEFINED |  |  | MCD | 1 | 3 | 5,6 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 73 | UNDEFINED |  |  | MCD | 1 | 3 | 7,8 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 74 | UNDEFINED |  |  | MCD | 1 | 3 | 9,10 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 75 | UNDEFINED |  |  | MCD | 1 | 3 | 11,12 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 76 | UNDEFINED |  |  | MCD | 1 | 3 | 13,14 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 77 | UNDEFINED |  |  | MCD | 1 | 4 | 1,2 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 78 | UNDEFINED |  |  | MCD | 1 | 4 | 3,4 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 79 | UNDEFINED |  |  | MCD | 1 | 4 | 5,6 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 80 | UNDEFINED |  |  | MCD | 1 | 4 | 7,8 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 81 | UNDEFINED |  |  | MCD | 1 | 4 | 9,10 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 82 | UNDEFINED |  |  | MCD | 1 | 4 | 11,12 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 83 | UNDEFINED |  |  | MCD | 1 | 4 | 13,14 | [8 empty] | Shown in EMS but not on point list. Field to verify RTU terms.
| I | 84 | SPT COMM FAIL |  | NM/ALM | [12 empty] | New point. | A

## Analog
| Update: | 2019-08-05 |  |  |  | RTU Type: |  |  |  | S-9000 via ASE Protocol Translator
TOMS RIVER (JC)
Pt. | DNP to EMS |  |  | RTU | TRWS9 to RTU |  | Scan | Card Location |  | I/O Panel |  |  |  | Terminations |  |  | CTR | PTR | EMS |  | XDCR
Own | Type | Pt. | Point Description | kV | FR | WD | Freq | Cage | Slot | PNL | TB+ | TB- | SHLD | PNL | TB | Term | X:1 | X:1 | FS | Qty | FS | Comments | Rev
| AI | 0 | SPARE |  | 0 | 1 |  | B1 | B2 | B2 | 1-3 | 1-4 | 1-2 | [6 empty] | CNTS | ±1mA | Keep index spare, was for AD Cal. | A
| AI | 1 | 4.8 kV VOLTAGE |  | 0 | 2 |  | B1 | B2 | B2 | 1-6 | 1-7 | 1-5 | [6 empty] | kV | ±1mA
| AI | 2 | BANK 1 MW |  | 0 | 3 |  | B1 | B2 | B2 | 1-9 | 1-10 | 1-8 | [5 empty] | 36 | MW | ±1mA
| AI | 3 | BANK 1 MVAR |  | 0 | 4 |  | B1 | B2 | B2 | 1-12 | 1-13 | 1-11 | [5 empty] | 36 | MVAR | ±1mA
| AI | 4 | BANK 2 MW |  | 1 | 1 |  | B1 | B2 | B2 | 1-15 | 1-16 | 1-14 | [5 empty] | 36 | MW | ±1mA
| AI | 5 | BANK 2 MVAR |  | 1 | 2 |  | B1 | B2 | B2 | 2-3 | 2-4 | 2-2 | [5 empty] | 36 | MVAR | ±1mA
| AI | 6 | D212 34.5 kV VOLTAGE |  | 1 | 3 |  | B1 | B2 | B2 | 2-6 | 2-7 | 2-5 |  |  |  |  | 500 |  | kV | ±1mA
| AI | 7 | V126-1 34.5 kV VOLTAGE |  | 1 | 4 |  | B1 | B2 | B2 | 2-9 | 2-10 | 2-8 | [5 empty] | 45 | kV | ±1mA