## Revisions
HORNERSTOWN SUBSTATION (JC)
EMS Information
RTU Name: | HRNRSTNJ | ASE SPT Physical Communication Ports
FEP Number: | RF0 | Communication
FEP Channel: | 76 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
RTU Address: | 10220 | Port 1: | DNP | 10220 | 10 | JC EMS 9600 Baud | Cellular Modem, Dedicated
RTU Size: |  | Port 2: | Not used
|  | Port 3: | TRWS9 | 30 | 1 | RTU, 2400 baud | RS232/Modem
RTU Information |  | Port 4: | Not used
RTU Type*: | Alert 9000 (S9000) with front end ASE Protocol Translator
Firmware:
Powered At: | 48 VDC
Peripherals:
Station Phone: | 609/758-8930
Station Address:
Latitude: | 40° 6’ 41”
Longtitude: | 74° 30’ 43” |  |  | Rev | Date | Description | Rev. By
|  |  |  | A | 2018-12-05 | RTU being converted to DNP and cutover to CDMA dedicated circuit via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF1C033). LCR WBS#XIT-ED-000001-JC-1. | H. Riley (BMcD)
|  |  |  | B | 2019-02-14 | Config Updates for Points List Rev A - Upgrade Transport Equipment to Cellular Modem WO#16063703. - Updated DNP Comm circuit listing to Cellular Modem per new standard. Config HORNERSTOWN ASE SPT TRWS9000 DNP Rev A.xml | Bivins/BMcD

## Control
| Update: | 2/14/2019 | [8 empty] | RTU Type: | Alert 9000 (S9000) with front end ASE Protocol Translator
HORNERSTOWN SUBSTATION (JC)
Pt. | DNP to EMS |  | RTU |  | TRWS9 to RTU |  | Card |  | Relay Interface |  |  | Customer Termination |  |  | Comments | Rev
Own | Type | Pt | Point Description | Func | GRP | RLY | Cage | Slot | PNL | TB | Term | PNL | TB | Term
| C | 0 | ADAPTIVE RELAYING | OFF | 1 | 1 | 1A1 | 5 | 2A5 | TB1 | 1,2 | 2A6 | 1 | 1,2
| C | 0 | ADAPTIVE RELAYING | ON | 1 | 2 | 1A1 | 5 | 2A5 | TB1 | 3,4 | 2A6 | 1 | 3,4
| C | 1 | H60-2 LBSW | OPEN | 1 | 3 | 1A1 | 5 | 2A5 | TB1 | 5,6 | 2A6 | 1 | 5,6
| C | 1 | H60-2 LBSW | CLOSE | 1 | 4 | 1A1 | 5 | 2A5 | TB1 | 7,8 | 2A6 | 1 | 7,8
| C | 2 | H60-3 LBSW | OPEN | 1 | 5 | 1A1 | 5 | 2A5 | TB1 | 9,10 | 2A6 | 2 | 1,2
| C | 2 | H60-3 LBSW | CLOSE | 1 | 6 | 1A1 | 5 | 2A5 | TB1 | 11,12 | 2A6 | 2 | 3,4
| C | 3 | 67291 OCB | OPEN | 1 | 7 | 1A1 | 5 | 2A5 | TB1 | 13,14 | 2A6 | 2 | 5,6
| C | 3 | 67291 OCB | CLOSE | 1 | 8 | 1A1 | 5 | 2A5 | TB1 | 15,16 | 2A6 | 2 | 7,8
| C | 4 | 67292 VCB | OPEN | 1 | 9 | 1A1 | 5 | 2A5 | TB2 | 1,2 | 2A6 | 3 | 1,2
| C | 4 | 67292 VCB | CLOSE | 1 | 10 | 1A1 | 5 | 2A5 | TB2 | 3,4 | 2A6 | 3 | 3,4
| C | 5 | SPARE | TRWS9 to RTU GRP: INFORMATION MISSING FROM ORIGINAL ALERT 9000 PT LIST | Updated to Match EMS | A
| C | 5 | SPARE | [11 empty] | Updated to Match EMS | A
| C | 6 | SPARE | [11 empty] | Updated to Match EMS | A
| C | 6 | SPARE | [11 empty] | Updated to Match EMS | A
| C | 7 | SPARE | [11 empty] | Updated to Match EMS | A
| C | 7 | SPARE | [11 empty] | Updated to Match EMS | A

## Status
Update: | 2/14/2019 | [8 empty] | RTU Type: | Alert 9000 (S9000) with front end ASE Protocol Translator
HORNERSTOWN SUBSTATION (JC)
Pt. | DNP to EMS |  | RTU |  | Device Type | TRWS9 to RTU |  |  | Card |  | I/O Panel |  |  | Termination
Own | Type | Pt. | Point Description | Func |  | FR | WD | Bit | Cage | Slot | PNL | Input | -24 VDC | PNL | TB | Term | Comments | Rev
| C&I | 0 | 67291 OCB | OP/CL | CD | 0 | 1 | 1,2 | 1A1 | 11 | 1A6 | 5-1 | 5-2 | wired directly to 1A6
| C&I | 1 | 67292 VCB | OP/CL | CD | 0 | 1 | 3,4 | 1A1 | 11 | 1A6 | 5-3 | 5-4 | wired directly to 1A6
| C&I | 2 | SPARE |  | CD | 0 | 1 | 5,6 | 1A1 | 11 | 1A6 | 5-5 | 5-6 | wired directly to 1A6
| C&I | 3 | SPARE |  | CD | 0 | 1 | 7,8 | 1A1 | 11 | 1A6 | 5-7 | 5-8 | wired directly to 1A6
| C&I | 4 | SPARE |  | CD | 0 | 1 | 9,10 | 1A1 | 11 | 1A6 | 5-9 | 5-10 | wired directly to 1A6
| C&I | 5 | SPARE |  | CD | 0 | 1 | 11,12 | 1A1 | 11 | 1A6 | 5-11 | 5-12 | wired directly to 1A6
| C&I | 6 | SPARE |  | CD | 0 | 1 | 13,14 | 1A1 | 11 | 1A6 | 5-13 | 5-14 | wired directly to 1A6
| C&I | 7 | SPARE |  | CD | 0 | 1 | 15,16 | 1A1 | 11 | 1A6 | 5-15 | 5-16 | wired directly to 1A6
| C&I | 8 | SPARE |  | CD | 0 | 2 | 1,2 | 1A1 | 12 | 1A6 | 6-1 | 6-2 | wired directly to 1A6
| C&I | 9 | SPARE |  | CD | 0 | 2 | 3,4 | 1A1 | 12 | 1A6 | 6-3 | 6-4 | wired directly to 1A6
| C&I | 10 | SPARE |  | CD | 0 | 2 | 5,6 | 1A1 | 12 | 1A6 | 6-5 | 6-6 | wired directly to 1A6
| C&I | 11 | SPARE |  | CD | 0 | 2 | 7,8 | 1A1 | 12 | 1A6 | 6-7 | 6-8 | wired directly to 1A6
| C&I | 12 | SPARE |  | CD | 0 | 2 | 9,10 | 1A1 | 12 | 1A6 | 6-9 | 6-10 | wired directly to 1A6
| C&I | 13 | SPARE |  | CD | 0 | 2 | 11,12 | 1A1 | 12 | 1A6 | 6-11 | 6-12 | wired directly to 1A6
| I | 14 | H60-2 LBSW | CL/OP | NL | 0 | 3 | 1 | 1A1 | 13 | 1A6 | 7-1 | 7-2 | wired directly to 1A6
| I | 15 | H60-2 LBSW | OP/CL | NL | 0 | 3 | 2 | 1A1 | 13 | 1A6 | 7-3 | 7-4 | wired directly to 1A6
| I | 16 | H60-3 LBSW | CL/OP | NL | 0 | 3 | 3 | 1A1 | 13 | 1A6 | 7-5 | 7-6 | wired directly to 1A6
| I | 17 | H60-3 LBSW | OP/CL | NL | 0 | 3 | 4 | 1A1 | 13 | 1A6 | 7-7 | 7-8 | wired directly to 1A6
| I | 18 | SPARE-SCAN1 |  | NL | 0 | 3 | 5 | 1A1 | 13 | 1A6 | 7-9 | 7-10 | wired directly to 1A6
| I | 19 | ADAPTIVE RELAYING | OFF/ON | NL | 0 | 3 | 6 | 1A1 | 13 | 1A6 | 7-11 | 7-12 | wired directly to 1A6
| I | 20 | SPARE |  | NL | 0 | 3 | 7 | 1A1 | 13 | 1A6 | 7-13 | 7-14 | wired directly to 1A6
| I | 21 | SPARE |  | NL | 0 | 3 | 8 | 1A1 | 13 | 1A6 | 7-15 | 7-16 | wired directly to 1A6
| I | 22 | SPARE |  | NL | 0 | 3 | 9 | 1A1 | 14 | 1A6 | 8-1 | 8-2 | wired directly to 1A6
| I | 23 | SPARE |  | NL | 0 | 3 | 10 | 1A1 | 14 | 1A6 | 8-3 | 8-4 | wired directly to 1A6
| I | 24 | SPARE |  | NL | 0 | 3 | 11 | 1A1 | 14 | 1A6 | 8-5 | 8-6 | wired directly to 1A6
| I | 25 | SPARE |  | NL | 0 | 3 | 12 | 1A1 | 14 | 1A6 | 8-7 | 8-8 | wired directly to 1A6
| I | 26 | BATTERY | NM/ALM | NL | 0 | 3 | 13 | 1A1 | 14 | 1A6 | 8-9 | 8-10 | wired directly to 1A6
| I | 27 | LOCAL/REMOTE | LOC/REM | NL | 0 | 3 | 14 | 1A1 | 14 | 1A6 | 8-11 | 8-12 | wired directly to 1A6
| I | 28 | SPARE |  | INFORMATION MISSING FROM ORIGINAL ALERT 9000 PT LIST | [11 empty] | Updated to Match EMS | A
| I | 29 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 30 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 31 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 32 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 33 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 34 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 35 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 36 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 37 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 38 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 39 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 40 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 41 | SPARE | [13 empty] | Updated to Match EMS | A
| I | 42 | SPT COMM FAIL | NM/ALM | SPT INTERNAL INDICATION | [11 empty] | New Point | A

## Analog
| Update: | 2/14/2019 | [9 empty] | RTU Type: | Alert 9000 (S9000) with front end ASE Protocol Translator
HORNERSTOWN SUBSTATION (JC)
Pt. | DNP to EMS |  | RTU | TRWS9 to RTU |  |  | Card |  | I/O Panel |  |  |  | Terminations |  |  | CTR | VTR | EMS |  | XDCR
Own | Type | Pt. | Point Description | Frame | Word | Scan Seq | Cage | Slot | PNL | TB+ | TB- | SHLD | PNL | TB | Term | X:1 | X:1 | FS | Qty | FS | Comments | Rev
| AI | 0 | SPARE | 0 | 1 | 30 |  |  | 2A4 | 2-1 | 2-2 | 3-1 | [6 empty] | CNTS |  | TRWS9 90% SCALE Calibration, keep index spare. | A
| AI | 1 | SPARE | 0 | 2 | 30 |  |  | 2A4 | 2-3 | 2-4 | 3-3 | [6 empty] | CNTS |  | TRWS9 10% SCALE Calibration, keep index spare. | A
| AI | 2 | 67291 MW | 0 | 3 | 30 | 1A1 | 9 | 2A4 | 2-5 | 2-6 | 3-5 | [6 empty] | MW |  | FS=7.2
| AI | 3 | 67291 MVAR | 0 | 4 | 30 | 1A1 | 9 | 2A4 | 2-7 | 2-8 | 3-7 | [6 empty] | MX |  | FS=7.2
| AI | 4 | 67292 MW | 1 | 1 | 30 | 1A1 | 9 | 2A4 | 2-9 | 2-10 | 3-9 | [6 empty] | MW |  | FS=7.2
| AI | 5 | 67292 MVAR | 1 | 2 | 30 | 1A1 | 9 | 2A4 | 2-11 | 2-12 | 3-11 | [6 empty] | MX |  | FS=7.2
| AI | 6 | SPARE | 1 | 3 | 30 |  |  |  | 2-13 | 2-14 | 3-13
| AI | 7 | SPARE | 1 | 4 | 30 |  |  |  | 2-15 | 2-16 | 3-15
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)