## Revisions
Lacey (JC)
|  |  | Station Phone: |  | 609/693-8036
|  |  | Latitude: |  | 39° 49’ 58”
EMS Information |  |  | Longitude: |  | 74° 11’ 46”
RTU Name: | LACEY | ASE SPT Physical Communication Ports
FEP: | RF5 | Communication
Channel: | 82 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10210 | Port 1: | DNP | 10210 | 10 | JC EMS 9600 Baud | MPLS via 700MHz
|  | Port 2: | TRWS9 | 20 | 4 | RTU, 2400 baud | RS232/Modem
PLC Information |  | Port 3: | Not used
Processor Type: | None | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | S9000 with ASE Protocol Translator
Size:
Powered At: |  |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2018-10-10 | Converted to Excel format. RTU being converted to DNP and cutover to MPLS using 700MHz via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF1CH032). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted in red. LCR SAP#15628236. Config: Lacey ASE SPT TRWS9 DNP Rev A. | T. Belshe (BMcD)
|  |  |  | B | 2018-11-07 | RTU being converted to DNP and cutover to MPLS using 700MHz via ASE Protocol Translator. Updated RTU Address. Updated Control Point DNP to EMS numbering. LCR SAP#15628236. Config: Lacey ASE SPT TRWS9 DNP Rev A. | C. Davis (BMcD)
|  |  |  | C | 2019-02-18 | S9000 mapping updates. SPT Config Rev B. | Christiansen/BMcD

## Control
| Update: | 2019-02-18 |  |  | RTU Type: | S9000
Lacey (JC)
DNP to EMS |  | RTU | PTRW9550 to RTU |  | Customer Termination
Type | Pt | Point Description | Group | Relay | Inter-connection | Comments | Rev
C | 0 | SPARE | 0 | 0 | NONE | Updated to match EMS, was A/D Calibration 81% | A
C | 0 | SPARE | 0 | 1 | NONE | Updated to match EMS, A/D Calibration 27% | A
C | 1 | Z52 LBSW OPEN | 0 | 2 | 1A6-TB1 - 5,6
C | 1 | Z52 LBSW CLOSE | 0 | 3 | 1A6-TB1 - 7,8
C | 2 | NO 6 LBSW OPEN | 0 | 4 | 1A6-TB2 - 1,2
C | 2 | NO 6 LBSW CLOSE | 0 | 5 | 1A6-TB2 - 3,4
C | 3 | R144 LBSW OPEN | 0 | 6 | 1A6-TB2 - 5,6
C | 3 | R144 LBSW CLOSE | 0 | 7 | 1A6-TB2 - 7,8
C | 4 | BK 1 VCB OPEN | 0 | 8 | 1A6-TB3 - 1,2
C | 4 | BK 1 VCB CLOSE | 0 | 9 | 1A6-TB3 - 3,4
C | 5 | BK 2 VCB OPEN | 0 | 10 | 1A6-TB3 - 5,6
C | 5 | BK 2 VCB CLOSE | 0 | 11 | 1A6-TB3 - 7,8
C | 6 | BT VCB OPEN | 0 | 12 | 1A6-TB4 - 1,2
C | 6 | BT VCB CLOSE | 0 | 13 | 1A6-TB4 - 3,4
C | 7 | 67400 VCB OPEN | 0 | 14 | 1A6-TB4 - 5,6
C | 7 | 67400 VCB CLOSE | 0 | 15 | 1A6-TB4 - 7,8
C | 8 | 67401 VCB OPEN | 1 | 0 | 2A6-TB1 - 1,2
C | 8 | 67401 VCB CLOSE | 1 | 1 | 2A6-TB1 - 3,4
C | 9 | 67399 ACB OPEN | 1 | 2 | 2A6-TB1 - 5,6
C | 9 | 67399 ACB CLOSE | 1 | 3 | 2A6-TB1 - 7,8
C | 10 | 67398 ACB OPEN | 1 | 4 | 2A6-TB2 - 1,2
C | 10 | 67398 ACB CLOSE | 1 | 5 | 2A6-TB2 - 3,4
C | 11 | 5PCT VOLT RED OFF | 1 | 6 | 2A6-TB2 - 5,6 | Reordered to match EMS, field to verify wiring | A
C | 11 | 5PCT VOLT RED ON | 1 | 7 | 2A6-TB2 - 7,8 | Reordered to match EMS, field to verify wiring | A
C | 12 | ADAPTIVE RELAYING OFF | 1 | 8 | 2A6-TB3 - 1,2
C | 12 | ADAPTIVE RELAYING ON | 1 | 9 | 2A6-TB3 - 3,4
C | 13 | SPARE | 1 | 10
C | 13 | SPARE | 1 | 11
C | 14 | SPARE | 1 | 12
C | 14 | SPARE | 1 | 13
C | 15 | SPARE | 1 | 14
C | 15 | SPARE | 1 | 15

## Status
| Update: | 2019-02-18 | [6 empty] | RTU Type: | S9000
Lacey (JC)
Pt. | DNP TO EMS | [5 empty] | S9000 to RTU
Own | Type | Pt. | Point Description | Function | Type | Scan | Frame | Bit | Customer Termination | Comments | Rev
| I | 0 | Z52 LBSW | OPEN | I | A | 0 | 0 | 1A3-TB1 - 1
| I | 1 | Z52 LBSW | CLOSE | I | A | 0 | 1 | 1A3-TB1 - 2
| I | 2 | NO 6 LBSW | OPEN | I | A | 0 | 2 | 1A3-TB1 - 3
| I | 3 | NO 6 LBSW | CLOSE | I | A | 0 | 3 | 1A3-TB1 - 4
| I | 4 | R144 LBSW | OPEN | I | A | 0 | 4 | 1A3-TB1 - 5
| I | 5 | R144 LBSW | CLOSE | I | A | 0 | 5 | 1A3-TB1 - 6
| I | 6 | SPARE |  | I | A | 0 | 6 | 1A3-TB1 - 7
| I | 7 | SPARE |  | I | A | 0 | 7 | 1A3-TB1 - 8
| I | 8 | ADAPTIVE RELAYING | OFF/ON | I | A | 0 | 8 | 1A3-TB1 - 9
| I | 9 | 5PCT VOLT RED | OFF/ON | I | A | 0 | 9 | 1A3-TB1 - 10
| I | 10 | BK ALRM | NM/ALM | I | A | 0 | 10 | 1A3-TB1 - 11
| I | 11 | BATTERY | NM/ALM | I | A | 0 | 11 | 1A3-TB1 - 12
| I | 12 | LOCAL/REMOTE | LOC/REM | I | A | 0 | 12 | 1A3-TB1 - 13
| I | 13 | SPARE |  | I | A | 0 | 13 | 1A3-TB1 - 14
| I | 14 | SPARE |  | I | A | 0 | 14 | 1A3-TB4 - 1
| I | 15 | SPARE |  | I | A | 0 | 15 | 1A3-TB4 - 2
| I | 16 | SPARE |  | I | A | 0 | 16 | 1A3-TB4 - 3
| I | 17 | SPARE |  | I | A | 0 | 17 | 1A3-TB4 - 4
| I | 18 | SPARE |  | I | A | 0 | 18 | 1A3-TB4 - 5
| I | 19 | SPARE |  | I | A | 0 | 19 | 1A3-TB4- 6
| I | 20 | SPARE |  | I | A | 0 | 20 | 1A3-TB4 - 7
| I | 21 | SPARE |  | I | A | 0 | 21 | 1A3-TB4 - 8
| I | 22 | SPARE |  | I | A | 0 | 22 | 1A3-TB4 - 9
| I | 23 | SPARE |  | I | A | 0 | 23 | 1A3-TB4 - 10
| I | 24 | SPARE |  | I | A | 0 | 24 | 1A3-TB4 - 11
| I | 25 | SPARE |  | I | A | 0 | 25 | 1A3-TB4 - 12
| I | 26 | SPARE |  | I | A | 0 | 26 | 1A3-TB4 - 13
| I | 27 | SPARE |  | I | A | 0 | 27 | 1A3-TB4 - 14
| C & I | 28 | SPARE |  | II | A | 0 | 28, 29 | 1A3-TB2 - 1
| C & I | 29 | SPARE |  | II | A | 0 | 30, 31 | 1A3-TB2 - 2
| C & I | 30 | SPARE |  | II | A | 0 | 32,33 | 1A3-TB2 - 3
| C & I | 31 | SPARE |  | II | A | 0 | 34,35 | 1A3-TB2 - 4
| C & I | 32 | SPARE |  | II | A | 0 | 36,37 | 1A3-TB2 - 5
| C & I | 33 | SPARE |  | II | A | 0 | 38,39 | 1A3-TB2 - 6
| C & I | 34 | SPARE |  | II | A | 0 | 40,41 | 1A3-TB2 - 7
| C & I | 35 | 67400 VCB | CL/OP | II | A | 0 | 42,43 | 1A3-TB5 - 1
| C & I | 36 | 67401 VCB | CL/OP | II | A | 0 | 44,45 | 1A3-TB5 - 2
| C & I | 37 | 67399 ACB | CL/OP | II | A | 0 | 46,47 | 1A3-TB5 - 3
| C & I | 38 | 67398 ACB | CL/OP | II | A | 0 | 48,49 | 1A3-TB5 - 4
| C & I | 39 | BK 2 VCB | CL/OP | II | A | 0 | 50,51 | 1A3-TB5 - 5
| C & I | 40 | BT VCB | CL/OP | II | A | 0 | 52,53 | 1A3-TB5 - 6
| C & I | 41 | BK 1 VCB | CL/OP | II | A | 0 | 54,55 | 1A3-TB5 - 7
| I | 42 | SPT COMM FAIL | NM/ALM |  | NM/ALM | SPT INTERNAL INDICATION |  |  | New pt | A

## Analog
| Update: | 2019-02-18 | [6 empty] | RTU Type: | S9000
Lacey (JC)
Pt. | DNP to EMS |  |  | PTRW9550 to RTU
Own | Type | Pt. | Point Description | Frame | Word | Bit | Type | Scan | Customer Termination | Comments | Rev
| AI | 0 | SPARE | 0 | 1 | NA |  | C | None | AD Calibration, keep index spare | A
| AI | 1 | 12.5 kV | 0 | 2 | NA | A | C | 1A5-TB2 - 3,4
| AI | 2 | BK 1 MW | 0 | 3 | NA | A | C | 1A5-TB2 - 5,6
| AI | 3 | BK 1 MVAR | 0 | 4 | NA | A | C | 1A5-TB2 - 7,8
| AI | 4 | BK 2 MW | 1 | 1 | NA | A | C | 1A5-TB6 - 1,2
| AI | 5 | BK 2 MVAR | 1 | 2 | NA | A | C | 1A5-TB6 - 3,4
| AI | 6 | SPARE | 1 | 3 | NA | A | C | 1A5-TB6 - 5,6
| AI | 7 | SPARE | 1 | 4 | NA | A | C | 1A5-TB6 - 7,8
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)