## Revisions
RACEWAY MALL (JC)
|  |  | Station Phone: |  | 732-303-9803
|  |  | Latitude: |  | 40° 15’ 18”
EMS Information |  |  | Longitude: |  | 74° 18’ 18”
RTU Name: | RACEWAY | ASE SPT Physical Communication Ports
FEP: | RF0 | Communication
Channel: | 59 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10236 | Port 1: | DNP | 10236 | 10 | FE East EMS 9600 Baud | Cellular Serial
|  | Port 2: | TRWS9 | 20 | 3 | RTU, 1200 baud | RS232/Modem
PLC Information |  | Port 3: | Not used
Processor Type: |  | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | S-9000 via ASE Protocol Translator
Size:
Powered At: | 48 VDC |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-05-31 | Converted to Excel format. RTU being converted to DNP and cutover to Cellular Serial via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF1 CH18). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted in red. WO# 16036914. SCORES ID 104781. Reviewed by J.McLaughlin (BMcD); H.Riley/BMcD | J.McLaughlin/BMcD
Address |  |  |  | B | 2019-06-26 | Created config for ASE Protocol Translator for DNP and cutover to Cellular Serial per Points List Rev A. WO#16036914. Config Raceway Mall ASE SPT TRWS9 DNP Rev A. | A.Eisenbeisz/BMcD

## Control
| Update: | 2019-06-26 | [7 empty] | RTU Type: | S-9000 via ASE Protocol Translator
RACEWAY MALL (JC)
DNP to EMS |  |  |  |  | TRWS9 to RTU |  | Card Location |  | Relay | Customer
Type | Pt | Point Description | kV | Function | Relay Group | Relay | Cage | Slot | Interface | Termination | Comments | Rev
C | 0 | SPARE |  |  | 1 | 1 | 1A1 | 5 | 2A5-TB1-1,2 | 2A6-TB1-1,2 |  | A
C |  | SPARE |  |  | 1 | 2 | 1A1 | 5 | 2A5-TB1-3,4 | 2A6-TB1-3,4 |  | A
C | 1 | I87 LBSW |  | OPEN | 1 | 3 | 1A1 | 5 | 2A5-TB1-5,6 | 2A6-TB1-5,6 |  | A
C |  | I87 LBSW |  | CLOSE | 1 | 4 | 1A1 | 5 | 2A5-TB1-7,8 | 2A6-TB1-7,8 |  | A
C | 2 | NO 6 LBSW |  | OPEN | 1 | 5 | 1A1 | 5 | 2A5-TB1-9,10 | 2A6-TB2-1,2 |  | A
C |  | NO 6 LBSW |  | CLOSE | 1 | 6 | 1A1 | 5 | 2A5-TB1-11,12 | 2A6-TB2-3,4 |  | A
C | 3 | X752 LBSW |  | OPEN | 1 | 7 | 1A1 | 5 | 2A5-TB1-13,14 | 2A6-TB2-5,6 |  | A
C |  | X752 LBSW |  | CLOSE | 1 | 8 | 1A1 | 5 | 2A5-TB1-15,16 | 2A6-TB2-7,8 |  | A
C | 4 | SPARE |  | OPEN | 1 | 9 | 1A1 | 5 | 2A5-TB2-1,2 | 2A6-TB3-1,2 | Renamed to match EMS. Previous name NO 9 LBSW REMOVED 10/17/97 | A
C |  | SPARE |  | CLOSE | 1 | 10 | 1A1 | 5 | 2A5-TB2-3,4 | 2A6-TB3-3,4 | Renamed to match EMS. Previous name NO 9 LBSW REMOVED 10/17/97 | A
C | 5 | BK 1 VCB |  | OPEN | 1 | 11 | 1A1 | 5 | 2A5-TB2-5,6 | 2A6-TB3-5,6 |  | A
C |  | BK 1 VCB |  | CLOSE | 1 | 12 | 1A1 | 5 | 2A5-TB2-7,8 | 2A6-TB3-7,8 |  | A
C | 6 | BT VCB |  | OPEN | 1 | 13 | 1A1 | 5 | 2A5-TB2-9,10 | 2A6-TB4-1,2 |  | A
C |  | BT VCB |  | CLOSE | 1 | 14 | 1A1 | 5 | 2A5-TB2-11,12 | 2A6-TB4-3,4 |  | A
C | 7 | 47422 VCB |  | OPEN | 1 | 15 | 1A1 | 5 | 2A5-TB2-13,14 | 2A6-TB4-5,6 |  | A
C |  | 47422 VCB |  | CLOSE | 1 | 16 | 1A1 | 5 | 2A5-TB2-15,16 | 2A6-TB4-7,8 |  | A
C | 8 | 47424 VCB |  | OPEN | 2 | 1 | 1A1 | 5 | 2A5-TB4-1,2 | 2A7-TB1-1,2 |  | A
C |  | 47424 VCB |  | CLOSE | 2 | 2 | 1A1 | 5 | 2A5-TB4-3,4 | 2A7-TB1-3,4 |  | A
C | 9 | 47420 VCB |  | OPEN | 2 | 3 | 1A1 | 5 | 2A5-TB4-5,6 | 2A7-TB1-5,6 |  | A
C |  | 47420 VCB |  | CLOSE | 2 | 4 | 1A1 | 5 | 2A5-TB4-7,8 | 2A7-TB1-7,8 |  | A
C | 10 | BK 2 VCB |  | OPEN | 2 | 5 | 1A1 | 5 | 2A5-TB4-9,10 | 2A7-TB2-1,2 |  | A
C |  | BK 2 VCB |  | CLOSE | 2 | 6 | 1A1 | 5 | 2A5-TB4-11,12 | 2A7-TB2-3,4 |  | A
C | 11 | 47421 VCB |  | OPEN | 2 | 7 | 1A1 | 5 | 2A5-TB4-13,14 | 2A7-TB2-5,6 |  | A
C |  | 47421 VCB |  | CLOSE | 2 | 8 | 1A1 | 5 | 2A5-TB4-15,16 | 2A7-TB2-7,8 |  | A
C | 12 | 47423 VCB |  | OPEN | 2 | 9 | 1A1 | 5 | 2A5-TB4-1,2 | 2A7-TB3-1,2 |  | A
C |  | 47423 VCB |  | CLOSE | 2 | 10 | 1A1 | 5 | 2A5-TB4-3,4 | 2A7-TB3-3,4 |  | A
C | 13 | CAP 1 VCB |  | OPEN | 2 | 11 | 1A1 | 5 | 2A5-TB4-5,6 | 2A7-TB3-5,6 |  | A
C |  | CAP 1 VCB |  | CLOSE | 2 | 12 | 1A1 | 5 | 2A5-TB4-7,8 | 2A7-TB3-7,8 |  | A
C | 14 | ADAPTIVE RELAYING |  | OFF | 2 | 13 | 1A1 | 5 | 2A5-TB4-9,10 | 2A7-TB4-1,2 |  | A
C |  | ADAPTIVE RELAYING |  | ON | 2 | 14 | 1A1 | 5 | 2A5-TB4-11,12 | 2A7-TB4-3,4 |  | A
C | 15 | SPARE |  |  | 2 | 15 | 1A1 | 5 | 2A5-TB4-13,14 | 2A7-TB4-5,6 |  | A
C |  | SPARE |  |  | 2 | 16 | 1A1 | 5 | 2A5-TB4-15,16 | 2A7-TB4-7,8 |  | A
C | 16 | CAP 2 VCB |  | OPEN | 3 | 1 | 1A1 | 5 | 2A5-TB4-1,2 | 2A5-TB1-1,2 |  | A
C |  | CAP 2 VCB |  | CLOSE | 3 | 2 | 1A1 | 5 | 2A5-TB4-3,4 | 2A5-TB1-5,6 |  | A
C | 17 | 47425 VCB |  | OPEN | 3 | 3 | 1A1 | 5 | 2A5-TB4-5,6 | 2A5-TB4-9,10 |  | A
C |  | 47425 VCB |  | CLOSE | 3 | 4 | 1A1 | 5 | 2A5-TB4-7,8 | 2A5-TB4-13,14 |  | A
C | 18 | UNDEFINED |  |  | 3 | 5 | INFORMATION MISSING FROM ORIGINAL PT LIST |  |  |  | Updated to match EMS | A
C |  | UNDEFINED |  |  | 3 | 6 |  |  |  |  | Updated to match EMS | A
C | 19 | UNDEFINED |  |  | 3 | 7 |  |  |  |  | Updated to match EMS | A
C |  | UNDEFINED |  |  | 3 | 8 |  |  |  |  | Updated to match EMS | A
C | 20 | UNDEFINED |  |  | 3 | 9 |  |  |  |  | Updated to match EMS | A
C |  | UNDEFINED |  |  | 3 | 10 |  |  |  |  | Updated to match EMS | A
C | 21 | UNDEFINED |  |  | 3 | 11 |  |  |  |  | Updated to match EMS | A
C |  | UNDEFINED |  |  | 3 | 12 |  |  |  |  | Updated to match EMS | A
C | 22 | UNDEFINED |  |  | 3 | 13 |  |  |  |  | Updated to match EMS | A
C |  | UNDEFINED |  |  | 3 | 14 |  |  |  |  | Updated to match EMS | A
C | 23 | UNDEFINED |  |  | 3 | 15 |  |  |  |  | Updated to match EMS | A
C |  | UNDEFINED |  |  | 3 | 16 |  |  |  |  | Updated to match EMS | A

## Status
| Update: | 2019-06-26 | [5 empty] | RTU Type: |  | S-9000 via ASE Protocol Translator
RACEWAY MALL (JC)
Pt. | DNP to EMS |  |  |  |  | Type | TRWS9 to RTU |  |  | Card Location |  | I/O Panel |  | Customer
Own | Type | Pt | Point Description | kV | Function |  | FR | WD | Bit | Cage | Card Slot | Input TB | +24 VDC TB | Termination | Comments | Rev
| C&I | 0 | BK 1 VCB |  | OP/CL | CD | 0 | 1 | 1,2 | 1A1 | 11 | 5-1 | 5-2 | WIRE DIRECT TO 1A6 |  | A
| C&I | 1 | BT VCB |  | OP/CL | CD | 0 | 1 | 3,4 | 1A1 | 11 | 5-3 | 5-4 | WIRE DIRECT TO 1A6 |  | A
| C&I | 2 | 47422 VCB |  | OP/CL | CD | 0 | 1 | 5,6 | 1A1 | 11 | 5-5 | 5-6 | WIRE DIRECT TO 1A6 |  | A
| C&I | 3 | 47424 VCB |  | OP/CL | CD | 0 | 1 | 7,8 | 1A1 | 11 | 5-7 | 5-8 | WIRE DIRECT TO 1A6 |  | A
| C&I | 4 | 47420 VCB |  | OP/CL | CD | 0 | 1 | 9,10 | 1A1 | 11 | 5-9 | 5-10 | WIRE DIRECT TO 1A6 |  | A
| C&I | 5 | BK 2 VCB |  | OP/CL | CD | 0 | 1 | 11,12 | 1A1 | 11 | 5-11 | 5-12 | WIRE DIRECT TO 1A6 |  | A
| C&I | 6 | 47421 VCB |  | OP/CL | CD | 0 | 1 | 13,14 | 1A1 | 11 | 5-13 | 5-14 | WIRE DIRECT TO 1A6 |  | A
| C&I | 7 | SPARE |  |  | CD | 0 | 2 | 1,2 | 1A1 | 11 | 5-15 | 5-16 | WIRE DIRECT TO 1A6 |  | A
| C&I | 8 | 47423 VCB |  | OP/CL | CD | 0 | 2 | 3,4 | 1A1 | 12 | 6-1 | 6-2 | WIRE DIRECT TO 1A6 |  | A
| C&I | 9 | 47425 VCB |  | OP/CL | CD | 0 | 2 | 5,6 | 1A1 | 12 | 6-3 | 6-4 | WIRE DIRECT TO 1A6 |  | A
| C&I | 10 | SPARE |  |  | CD | 0 | 2 | 7,8 | 1A1 | 12 | 6-5 | 6-6 | WIRE DIRECT TO 1A6 |  | A
| C&I | 11 | SPARE |  |  | CD | 0 | 2 | 9,10 | 1A1 | 12 | 6-7 | 6-8 | WIRE DIRECT TO 1A6 |  | A
| C&I | 12 | SPARE |  |  | CD | 0 | 2 | 11,12 | 1A1 | 12 | 6-9 | 6-10 | WIRE DIRECT TO 1A6 |  | A
| C&I | 13 | SPARE |  |  | CD | 0 | 2 | 13,14 | 1A1 | 12 | 6-11 | 6-12 | WIRE DIRECT TO 1A6 |  | A
| I | 14 | I87 LBSW |  | CL/OP | NL | 0 | 3 | 1 | 1A1 | 13 | 7-1 | 7-2 | WIRE DIRECT TO 1A6 |  | A
| I | 15 | I87 LBSW |  | OP/CL | NL | 0 | 3 | 2 | 1A1 | 13 | 7-3 | 7-4 | WIRE DIRECT TO 1A6 |  | A
| I | 16 | NO 6 LBSW |  | CL/OP | NL | 0 | 3 | 3 | 1A1 | 13 | 7-5 | 7-6 | WIRE DIRECT TO 1A6 |  | A
| I | 17 | NO 6 LBSW |  | OP/CL | NL | 0 | 3 | 4 | 1A1 | 13 | 7-7 | 7-8 | WIRE DIRECT TO 1A6 |  | A
| I | 18 | X752 LBSW |  | CL/OP | NL | 0 | 3 | 5 | 1A1 | 13 | 7-9 | 7-10 | WIRE DIRECT TO 1A6 |  | A
| I | 19 | X752 LBSW |  | OP/CL | NL | 0 | 3 | 6 | 1A1 | 13 | 7-11 | 7-12 | WIRE DIRECT TO 1A6 |  | A
| I | 20 | ADAPTIVE RELAYING |  | OFF/ON | NL | 0 | 3 | 7 | 1A1 | 13 | 7-13 | 7-14 | WIRE DIRECT TO 1A6 |  | A
| I | 21 | SPARE |  |  | NL | 0 | 3 | 8 | 1A1 | 13 | 7-15 | 7-16 | WIRE DIRECT TO 1A6 | Renamed to match EMS. Previous name NO 9 LBSW REMOVED 10/17/97 | A
| I | 22 | CAP 1 VCB |  | OP/CL | NL | 0 | 3 | 9 | 1A1 | 14 | 8-1 | 8-2 | WIRE DIRECT TO 1A6 |  | A
| I | 23 | CAP 2 VCB |  | OP/CL | NL | 0 | 3 | 10 | 1A1 | 14 | 8-3 | 8-4 | WIRE DIRECT TO 1A6 |  | A
| I | 24 | BK 1 ALRM |  | NM/ALM | NL | 0 | 3 | 11 | 1A1 | 14 | 8-5 | 8-6 | WIRE DIRECT TO 1A6 |  | A
| I | 25 | BK 2 ALRM |  | NM/ALM | NL | 0 | 3 | 12 | 1A1 | 14 | 8-7 | 8-8 | WIRE DIRECT TO 1A6 |  | A
| I | 26 | 47425 RELAY FAIL |  | NM/ALM | NL | 0 | 3 | 13 | 1A1 | 14 | 8-9 | 8-10 | WIRE DIRECT TO 1A6 |  | A
| I | 27 | LOCAL/REMOTE |  | LOC/REM | NL | 0 | 3 | 14 | 1A1 | 14 | 8-11 | 8-12 | WIRE DIRECT TO 1A6 |  | A
| I | 28 | SPARE |  |  | NL | 0 | 4 | 1 | 1A4 | 7 | 1-1 | 2-1 | WIRE DIRECT TO 1A9 |  | A
| I | 29 | SPARE |  |  | NL | 0 | 4 | 2 | 1A4 | 7 | 1-2 | 2-2 | WIRE DIRECT TO 1A9 |  | A
| I | 30 | SPARE |  |  | NL | 0 | 4 | 3 | 1A4 | 7 | 1-3 | 2-3 | WIRE DIRECT TO 1A9 |  | A
| I | 31 | SPARE |  |  | NL | 0 | 4 | 4 | 1A4 | 7 | 1-4 | 2-4 | WIRE DIRECT TO 1A9 |  | A
| I | 32 | SPARE |  |  | NL | 0 | 4 | 5 | 1A4 | 7 | 1-5 | 2-5 | WIRE DIRECT TO 1A9 |  | A
| I | 33 | SPARE |  |  | NL | 0 | 4 | 6 | 1A4 | 7 | 1-6 | 2-6 | WIRE DIRECT TO 1A9 |  | A
| I | 34 | SPARE |  |  | NL | 0 | 4 | 7 | 1A4 | 7 | 1-7 | 2-7 | WIRE DIRECT TO 1A9 |  | A
| I | 35 | SPARE |  |  | NL | 0 | 4 | 8 | 1A4 | 7 | 1-8 | 2-8 | WIRE DIRECT TO 1A9 |  | A
| I | 36 | SPARE |  |  | NL | 0 | 4 | 9 | 1A4 | 8 | 3-1 | 2-16 | WIRE DIRECT TO 1A9 |  | A
| I | 37 | SPARE |  |  | NL | 0 | 4 | 10 | 1A4 | 8 | 3-2 | 2-15 | WIRE DIRECT TO 1A9 |  | A
| I | 38 | SPARE |  |  | NL | 0 | 4 | 11 | 1A4 | 8 | 3-3 | 2-14 | WIRE DIRECT TO 1A9 |  | A
| I | 39 | SPARE |  |  | NL | 0 | 4 | 12 | 1A4 | 8 | 3-4 | 2-13 | WIRE DIRECT TO 1A9 |  | A
| I | 40 | SPARE |  |  | NL | 0 | 4 | 13 | 1A4 | 8 |  |  |  |  | A
| I | 41 | SPARE |  |  | NL | 0 | 4 | 14 | 1A4 | 8 |  |  |  |  | A
| I | 42 | SPT COMM FAIL |  | NM/ALM | SPT INTERNAL INDICATION | [8 empty] | New point. | A

## Analog
| Update: | 2019-06-26 | [6 empty] | RTU Type: |  | S-9000 via ASE Protocol Translator
RACEWAY MALL (JC)
Pt. | DNP to EMS |  |  | RTU | Device | TRWS9 to RTU |  | Scan | Card Location |  | I/O Panel |  |  | Customer
Own | Type | Pt. | Point Description | kV | Type | FR | WD | Freq. | Cage | Slot | +TB | -TB | S TB | Termination | Comments | Rev
| AI | 0 | SPARE |  | CNTS | 0 | 1 | 30 | 1A4 | 9 | 1-1 | 1-2 | 2-1 |  | Spare 90PCT A/D CAL point upon project completion | A
| AI | 1 | SPARE |  | CNTS | 0 | 2 | 30 | 1A4 | 9 | 1-3 | 1-4 | 2-3 |  | Spare 10PCT A/D CAL point upon project completion | A
| AI | 2 | 12.5 kV |  | kV | 0 | 3 | 30 | 1A4 | 9 | 1-5 | 1-6 | 2-5 |  |  | A
| AI | 3 | BK 1 MW |  | MW | 0 | 4 | 30 | 1A4 | 9 | 1-7 | 1-8 | 2-7 |  |  | A
| AI | 4 | BK 1 MVAR |  | MX | 1 | 1 | 30 | 1A4 | 9 | 1-9 | 1-10 | 2-9 |  |  | A
| AI | 5 | BK 2 MW |  | MW | 1 | 2 | 30 | 1A4 | 9 | 1-11 | 1-12 | 2-11 |  |  | A
| AI | 6 | BK 2 MVAR |  | MX | 1 | 3 | 30 | 1A4 | 9 | 1-13 | 1-14 | 2-13 |  |  | A
| AI | 7 | 47420 MW |  | MW | 1 | 4 | 30 | 1A4 | 9 | 1-15 | 1-16 | 2-15 |  |  | A
| AI | 8 | 47421 MW |  | MW | 2 | 1 | 30 | 1A4 | 10 | 4-1 | 4-2 | 2-2 |  |  | A
| AI | 9 | 47422 MW |  | MW | 2 | 2 | 30 | 1A4 | 10 | 4-3 | 4-4 | 2-4 |  |  | A
| AI | 10 | 47423 MW |  | MW | 2 | 3 | 30 | 1A4 | 10 | 4-5 | 4-6 | 2-6 |  |  | A
| AI | 11 | 47424 MW |  | MW | 2 | 4 | 30 | 1A4 | 10 | 4-7 | 4-8 | 2-8 |  |  | A
| AI | 12 | I87 34.5 kV VOLTS | 34.5 | kV | 3 | 1 | 30 | 1A4 | 10 | 4-9 | 4-10 | 2-10 |  |  | A
| AI | 13 | X752 34.5 kV VOLTS | 34.5 | kV | 3 | 2 | 30 | 1A4 | 10 | 4-11 | 4-12 | 2-12 |  |  | A
| AI | 14 | SPARE |  |  | 3 | 3 | 30 |  | 10 | 4-13 | 4-14 | 2-14 |  |  | A
| AI | 15 | SPARE |  |  | 3 | 4 | 30 |  | 10 | 4-15 | 4-16 | 2-16 |  |  | A
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)