## Revisions
Alpha (JC)
|  |  | Latitude: |  | N40° 39' 55''
EMS Information |  |  | Longitude: |  | W75° 08' 51''
RTU Name: | ALPHA | ASE SPT Physical Communication Ports
FEP: | RF5 | Communication
Channel: | 85 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10235 | Port 1: | DNP | 10235 | 10 | JC EMS 9600 Baud | MPLS via 700MHz
|  | Port 2: | TRW9550 |  | 3 | RTU, 1200 baud | RS232
PLC Information |  | Port 3: | Not used
Processor Type: | n/a | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | ALERT RTU with ASE protocol translator
Size:
Powered At: |  |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-05-14 | RTU being converted to DNP and cutover to MPLS over 700MHz via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF1 Ch014). WO#15834642 SCORES 103727. Reviewed by H.Riley/BMcD | T. Belshe (BMcD)
Station Address: | 65 Industrial Road |  |  | B | 2019-05-17 | Added the local address to Port 1. Removed the local address for port 2. Added the address to column B9. Added the Full Scale column on the analog sheet. This is a revision for the same work completed in Rev A. WO#15834642 SCORES 103727 W.Blankenship/BMcD | W.Blankenship/BMcD
Alpha NJ 08865

## Control
| Update: | 2019-05-14 | [5 empty] | RTU Type: | TRW9550 via protocol translator
Alpha (JC)
DNP to EMS |  | RTU |  | Device type | TRW9550 to RTU
Type | Pt | Point Description | Function |  | Group | Control Bit | Relay Number | Bit Number | Comments | Rev
C | 0 | SPARE |  | CTL | 00 | 0 | K1 | --- |  | A
C |  | SPARE |  | CTL | 00 | 1 | K2 | --- |  | A
C | 1 | ADAPTIVE RELAYING | ON | CTL | 00 | 2 | K3 | --- |  | A
C |  | ADAPTIVE RELAYING | OFF | CTL | 00 | 3 | K4 | --- |  | A
C | 2 | Y25-1 LBSW | CL | CTL | 00 | 4 | K5 | --- |  | A
C |  | Y25-1 LBSW | OP | CTL | 00 | 5 | K6 | --- |  | A
C | 3 | Y25-2 LBSW | CL | CTL | 00 | 6 | K7 | --- | Updated to match EMS, field to verify | A
C |  | Y25-2 LBSW | OP | CTL | 00 | 7 | K8 | --- | Updated to match EMS, field to verify | A
C | 4 | 24687 ACB | CL | CTL | 00 | 8 | K9 | --- | Updated to match EMS, field to verify | A
C |  | 24687 ACB | OP | CTL | 00 | 9 | K10 | --- | Updated to match EMS, field to verify | A
C | 5 | 24688 ACB | CL | CTL | 00 | 10 | K11 | --- | Updated to match EMS, field to verify | A
C |  | 24688 ACB | OP | CTL | 00 | 11 | K12 | --- | Updated to match EMS, field to verify | A
C | 6 | 24689 ACB | CL | CTL | 00 | 12 | K13 | --- | Updated to match EMS, field to verify | A
C |  | 24689 ACB | OP | CTL | 00 | 13 | K14 | --- | Updated to match EMS, field to verify | A
C | 7 | NO 6 LBSW | CL | CTL | 00 | 14 | K15 | --- | Updated to match EMS, field to verify | A
C |  | NO 6 LBSW | OP | CTL | 00 | 15 | K16 | --- | Updated to match EMS, field to verify | A
C | 8 | BK 2 VCB | CL | CTL | 01 | 0 | K1 | --- |  | A
C |  | BK 2 VCB | OP | CTL | 01 | 1 | K2 | --- |  | A
C | 9 | 27690 VCB | CL | CTL | 01 | 2 | K3 | --- |  | A
C |  | 27690 VCB | OP | CTL | 01 | 3 | K4 | --- |  | A
C | 10 | 27691 VCB | CL | CTL | 01 | 4 | K5 | --- |  | A
C |  | 27691 VCB | OP | CTL | 01 | 5 | K6 | --- |  | A
C | 11 | 27692 VCB | CL | CTL | 01 | 6 | K7 | --- |  | A
C |  | 27692 VCB | OP | CTL | 01 | 7 | K8 | --- |  | A
C | 12 | BT-FUT VCB | CL | CTL | 01 | 8 | K9 | --- |  | A
C |  | BT-FUT VCB | OP | CTL | 01 | 9 | K10 | --- |  | A
C | 13 | 5PCT VOLT RED | ON | CTL | 01 | 10 | K11 | --- | Updated to match EMS, field to verify | A
C |  | 5PCT VOLT RED | OFF | CTL | 01 | 11 | K12 | --- | Updated to match EMS, field to verify | A
C | 14 | SPARE |  |  | Information missing from previous points list |  |  |  |  | A
C |  | SPARE | [7 empty] | A
C | 15 | SPARE | [7 empty] | A
C |  | SPARE | [7 empty] | A

## Status
| Update: | 2019-05-14 | [5 empty] | RTU Type: | TRW9550 via protocol translator
Alpha (JC)
Pt. | DNP TO EMS |  |  |  | TRW9550 to RTU
Own | Type | Pt. | Point Description | Function | Type | Frame | Bit | Seq No. | Bit No. | Comments | Rev
| I | 0 | LOCAL/REMOTE | LOC/REM | SS | 00 | 0 | 30 | 0 |  | A
| I | 1 | BATTERY | NM/ALM | SS | 00 | 1 | 30 | 1 |  | A
| I | 2 | Y25-1 LBSW | CL/OP | SS | 00 | 2 | 30 | 2 | Updated function for b status, field to verify | A
| I | 3 | Y25-1 LBSW | OP/CL | SS | 00 | 3 | 30 | 3 |  | A
| I | 4 | Y25-2 LBSW | CL/OP | SS | 00 | 4 | 30 | 4 | Updated function for b status, field to verify | A
| I | 5 | Y25-2 LBSW | OP/CL | SS | 00 | 5 | 30 | 5 |  | A
| I | 6 | NO 6 LBSW | CL/OP | SS | 00 | 6 | 30 | 6 | Updated function for b status, field to verify | A
| I | 7 | NO 6 LBSW | OP/CL | SS | 00 | 7 | 30 | 7 |  | A
| I | 8 | 5PCT VOLT RED | OFF/ON | SS | 00 | 8 | 30 | 8 | Updated to match EMS, field to verify | A
| I | 9 | DX RELAY FAIL | NM/ALM | SS | 00 | 9 | 30 | 9 |  | A
| I | 10 | BK 2 ALMS | NM/ALM | SS | 00 | 10 | 30 | 10 |  | A
| I | 11 | ADAPTIVE RELAYING | OFF/ON | SS | 00 | 11 | 30 | 11 |  | A
| I | 12 | SPARE |  | SS | 00 | 12 | 30 | 12 |  | A
| I | 13 | SPARE |  | SS | 00 | 13 | 30 | 13 |  | A
| I | 14 | SPARE |  | SS | 00 | 14 | 30 | 14 |  | A
| I | 15 | SPARE |  | SS | 00 | 15 | 30 | 15 |  | A
| C & I | 16 | 24687 ACB | OP/CL | 2B | 00 | 01 | 00 | 0,8 |  | A
| C & I | 17 | 24688 ACB | OP/CL | 2B | 00 | 01 | 00 | 1,9 |  | A
| C & I | 18 | 24689 ACB | OP/CL | 2B | 00 | 01 | 00 | 2,10 |  | A
| C & I | 19 | BK1 OIL SPILL | NM/ALM | 2B | 00 | 01 | 00 | 3,11 |  | A
| C & I | 20 | BK 2 VCB | OP/CL | 2B | 00 | 01 | 00 | 4,12 |  | A
| C & I | 21 | 27690 VCB | OP/CL | 2B | 00 | 01 | 00 | 5,13 |  | A
| C & I | 22 | 27691 VCB | OP/CL | 2B | 00 | 01 | 00 | 6,14 |  | A
| C & I | 23 | 27692 VCB | OP/CL | 2B | 00 | 01 | 00 | 7,15 |  | A
| C & I | 24 | BT-FUT VCB | OP/CL | 2B | 00 | 02 | 01 | 0,8 |  | A
| C & I | 25 | SPARE |  | 2B | 00 | 02 | 01 | 1,9 |  | A
| C & I | 26 | SPARE |  | 2B | 00 | 02 | 01 | 2,10 |  | A
| C & I | 27 | SPARE |  | 2B | 00 | 02 | 01 | 3,11 |  | A
| C & I | 28 | SPARE |  | 2B | 00 | 02 | 01 | 4,12 |  | A
| C & I | 29 | SPARE |  | 2B | 00 | 02 | 01 | 5,13 |  | A
| C & I | 30 | SPARE |  | 2B | 00 | 02 | 01 | 6,14 |  | A
| C & I | 31 | SPARE |  | 2B | 00 | 02 | 01 | 7,15 |  | A
| I | 32 | SPT COMM FAIL | NM/ALM | SPT INTERNAL INDICATION |  |  |  |  | New pt | A

## Analog
| Update: | 2019-05-14 |  |  |  |  | RTU Type: |  |  | TRW9550 via protocol translator
Alpha (JC)
Pt. | DNP to EMS |  |  | TRW9550 to RTU |  |  |  | EMS Full Scale
Own | Type | Pt. | Point Description | Frame | Word | Seq No. | Bit No. | Raw | Eng | Qty | Comments | Rev
| AI | 0 | SPARE | 00 | 0 | 80 | --- | 2047 | 2047 | NA | Spare 90PCT A/D CAL, keep index spare | B
| AI | 1 | SPARE | 00 | 1 | 81 | --- | 2047 | 2047 | NA | Spare 10PCT A/D CAL, keep index spare | B
| AI | 2 | 4.8 KV | 00 | 2 | 82 | --- | 2047 | 6 | KV |  | B
| AI | 3 | 12.5 KV | 00 | 3 | 83 | --- | 2047 | 15.6 | KV |  | B
| AI | 4 | BK 2 MW | 01 | 0 | 84 | --- | 2047 | 21.6 | MW |  | B
| AI | 5 | BK 2 MVAR | 01 | 1 | 85 | --- | 2047 | 21.6 | MVAR |  | B
| AI | 6 | 27690 MW | 01 | 2 | 86 | --- | 2047 | 10.8 | MW |  | B
| AI | 7 | 27690 MVAR | 01 | 3 | 87 | --- | 2047 | 10.8 | MVAR |  | B
| AI | 8 | 27690 KV | 02 | 0 | 88 | --- | 2047 | 15.6 | KV |  | B
| AI | 9 | 27691 MW | 02 | 1 | 89 | --- | 2047 | 10.8 | MW |  | B
| AI | 10 | 27691 MVAR | 02 | 2 | 8A | --- | 2047 | 10.8 | MVAR |  | B
| AI | 11 | 27691 KV | 02 | 3 | 8B | --- | 2047 | 15.6 | KV |  | B
| AI | 12 | 27692 MW | 03 | 0 | 8C | --- | 2047 | 10.8 | MW |  | B
| AI | 13 | 27692 MVAR | 03 | 1 | 8D | --- | 2047 | 10.8 | MVAR |  | B
| AI | 14 | 27692 KV | 03 | 2 | 8E | --- | 2047 | 15.6 | KV |  | B
| AI | 15 | SPARE | 03 | 3 | 8F | --- | 2047 | 0 | NA |  | B