## Revisions
Moore (JC)
|  |  | Station Phone: |  | 609-737-7748
|  |  | Latitude: |  | N40 19 30
EMS Information |  |  | Longitude: |  | W74 54 56
RTU Name: | Moore_J | ASE SPT Physical Communication Ports
FEP: | RF0 | Communication
Channel: | 58 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10191 | Port 1: | DNP | 10191 | 10 | JC EMS 9600 Baud | CDMA Dedicated
|  | Port 2: | TRW9550 | 30 | 3 | RTU, 2400 baud | RS232/Modem
PLC Information |  | Port 3: | Not used
Processor Type: | None | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | 9550 (with front end ASE Protocol Translator)
Size:
Powered At: |  |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2018-09-13 | Converted to Excel format. RTU being converted to DNP and cutover to CDMA dedicated circuit via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH MF1C008). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted in red. LCR SAP#15863607 Reviewed by H. Riley (BMcD) | T. Belshe (BMcD)
|  |  |  | B | 2018-10-24 | Created config and updated SPT information in status and control tabs, moved RTU from port 3 to port 2. Config: Rev A | KAK/BMcD

## Control
| Update: | 10/24/2018 | [5 empty] | RTU Type: | 9550 (with front end ASE Protocol Translator)
Moore (JC)
DNP to EMS |  | RTU |  |  | TRW9550 to RTU |  |  | Control
Type | Pt | Point Description | kV | Function | Group | Control Bit | Relay Number | Inter-connection | Comments | Rev
C | 0 | SPARE |  |  | 00 | 0 | K1
C | 0 | SPARE |  |  | 00 | 1 | K1
C | 1 | SPARE |  |  | 00 | 2 | K2
C | 1 | SPARE |  |  | 00 | 3 | K2
C | 2 | 24603 OCB |  | CLOSE | 00 | 4 | K3
C | 2 | 24603 OCB |  | OPEN | 00 | 5 | K3
C | 3 | 24588 OCB |  | CLOSE | 00 | 6 | K4
C | 3 | 24588 OCB |  | OPEN | 00 | 7 | K4
C | 4 | SPARE |  |  | 00 | 8 | K5 |  | Updated to match EMS, was Cap 1 OCB on old pt list | A
C | 4 | SPARE |  |  | 00 | 9 | K5 |  | Updated to match EMS, was Cap 1 OCB on old pt list | A
C | 5 | SPARE |  |  | 00 | 10 | K6 |  |  | B
C | 5 | SPARE |  |  | 00 | 11 | K6 |  |  | B
C | 6 | SPARE |  |  | 00 | 12 | K7 |  |  | B
C | 6 | SPARE |  |  | 00 | 13 | K7 |  |  | B
C | 7 | SPARE |  |  | 00 | 14 | K8 |  |  | B
C | 7 | SPARE |  |  | 00 | 15 | K8 |  |  | B

## Status
| Update: | 10/24/2018 |  |  | RTU Type: | 9550 (with front end ASE Protocol Translator)
Moore (JC)
Pt. | DNP TO EMS |  |  |  | TRW9550 to RTU
Own | Type | Pt. | Point Description | Function | Frame | Bit No. | Comments | Rev
| I | 0 | LOCAL/REMOTE | LOC/REM | 00 | 0
| I | 1 | BATTERY | NM/ALM | 00 | 1
| I | 2 | SPARE |  | 00 | 2
| I | 3 | SPARE |  | 00 | 3
| I | 4 | SPARE |  | 00 | 4
| I | 5 | SPARE |  | 00 | 5
| I | 6 | SPARE |  | 00 | 6
| I | 7 | SPARE |  | 00 | 7
| I | 8 | SPARE |  | 00 | 8
| I | 9 | SPARE |  | 00 | 9
| I | 10 | SPARE |  | 00 | 10
| I | 11 | SPARE |  | 00 | 11
| I | 12 | SPARE |  | 00 | 12
| I | 13 | SPARE |  | 00 | 13
| I | 14 | SPARE |  | 00 | 14
| I | 15 | SPARE |  | 00 | 15
| C&I | 16 | 24603 OCB | OP/CL | 00 | 16,17 |  | B
| C&I | 17 | 24588 OCB | OP/CL | 00 | 18,19 |  | B
| C&I | 18 | SPARE |  | 00 | 20,21 | Updated to match EMS, was Cap 1 OCB on old pt list | A
| C&I | 19 | OIL SPILL ALRM | NM/ALM | 00 | 22,23 |  | B
| C&I | 20 | SPARE |  | 00 | 24,25 |  | B
| C&I | 21 | SPARE |  | 00 | 26,27 |  | B
| C&I | 22 | SPARE |  | 00 | 28,29 |  | B
| C&I | 23 | SPARE |  | 00 | 30,31 |  | B
| C&I | 24 | SPARE |  | 00 | 32,33 |  | B
| C&I | 25 | SPARE |  | 00 | 34,35 |  | B
| C&I | 26 | SPARE |  | 00 | 36,37 |  | B
| C&I | 27 | SPARE |  | 00 | 38,39 |  | B
| C&I | 28 | SPARE |  | 00 | 40,41 |  | B
| C&I | 29 | SPARE |  | 00 | 42,43 |  | B
| C&I | 30 | SPARE |  | 00 | 44,45 |  | B
| C&I | 31 | SPARE |  | 00 | 46,47 |  | B
| I | 32 | SPT COMM FAIL | NM/ALM | SPT INTERNAL INDICATION |  | New Point | A

## Analog
| Update: | 10/24/2018 |  |  |  | 8/8/2018 |  |  | RTU Type: | TRW9550
Moore (JC)
Pt. | DNP TO EMS |  |  |  | TRW9550 to RTU
Own | Type | Pt. | Point Description | Function | Frame | Word | Seq No. | Bit No. | Comments | Rev
| AI | 0 | SPARE |  | 00 | 0 | 80 | --- | CDC II FULL SCALE Calibration, keep index spare. | A
| AI | 1 | SPARE |  | 00 | 1 | 81 | --- | CDC II ZERO SCALE Calibration, keep index spare. | A
| AI | 2 | 4.8 KV |  | 00 | 2 | 82 | ---
| AI | 3 | SPARE |  | 00 | 3 | 83 | ---
| AI | 4 | SPARE |  | 01 | 0 | 84 | ---
| AI | 5 | SPARE |  | 01 | 1 | 85 | ---
| AI | 6 | SPARE |  | 01 | 2 | 86 | ---
| AI | 7 | SPARE |  | 01 | 3 | 87 | ---
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)