## Revisions
Stanton (JC)
|  |  | Station Phone: |  | 908-806-3839
|  |  | Latitude: |  | N40° 34' 12''
EMS Information |  |  | Longitude: |  | W74° 51' 37''
RTU Name: | STANTONJ | ASE SPT Physical Communication Ports
FEP: | RF5 | Communication
Channel: | 78 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 10228 | Port 1: | DNP | 10228 | 10 | JC EMS 9600 Baud | MPLS via 700MHz
|  | Port 2: | TRW9550 | 20 | 3 | RTU, 1200 baud | RS232/Modem
PLC Information |  | Port 3: | Not used
Processor Type: | n/a | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | Outpost 9550 with front end ASE Protocol Translator
Size:
Powered At: |  |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-01-24 | RTU being converted to DNP and cutover to MPLS via 700MHz radio through an ASE Protocol Translator. Updated baud rate and FEP/CH (old FEP/CH MF1CH009). Discrepancies from existing pt list to EMS were updated to match EMS and highlighted in red. Network #XIT-ED-000001-JC-1. Reviewed by H. Riley/BMcD | T. Belshe (BMcD)
|  |  |  | B | 2019-05-06 | Created SPT config for Points list Rev A. Upgraded Transport equipment for MPLS via 700MHz at 9600 baud. Config: STANTON SPT DNP 9550 Rev A. | A.Eisenbeisz (BMcD)

## Control
| Update: | 5/6/2019 |  |  |  | RTU Type: |  | RTU Type: | Outpost 9550 with front end ASE Protocol Translator
Stanton (JC)
DNP to EMS |  | RTU |  |  | TRW9550 to RTU
Type | Pt | Point Description | kV | Function | Group | Control Bit | Relay Number | Bit Number | Comments | Rev
C | 0 | SPARE |  |  | 01 | 15 | K1 | ---
C |  | SPARE |  |  | 01 | 14 | K2 | ---
C | 1 | SPARE |  |  | 01 | 13 | K3 | ---
C |  | SPARE |  |  | 01 | 12 | K4 | ---
C | 2 | F734-1 LBSW |  | Close | 01 | 11 | K5 | ---
C |  | F734-1 LBSW |  | Open | 01 | 10 | K6 | ---
C | 3 | NO 6 LBSW |  | Close | 01 | 9 | K7 | ---
C |  | NO 6 LBSW |  | Open | 01 | 8 | K8 | ---
C | 4 | F734-3 LBSW |  | Close | 01 | 7 | K9 | ---
C |  | F734-3 LBSW |  | Open | 01 | 6 | K10 | ---
C | 5 | BK 2 VCB |  | Close | 01 | 5 | K11 | ---
C |  | BK 2 VCB |  | Open | 01 | 4 | K12 | ---
C | 6 | 27401 VCB |  | Close | 01 | 3 | K13 | ---
C |  | 27401 VCB |  | Open | 01 | 2 | K14 | ---
C | 7 | 27404 VCB |  | Close | 01 | 1 | K15 | ---
C |  | 27404 VCB |  | Open | 01 | 0 | K16 | ---
C | 8 | SPARE |  | Close | 02 | 15 | K1 | --- | Point updated to match EMS, was showing BT 12.5 VCB on legacy pt list. Field to verify.
C |  | SPARE |  | Open | 02 | 14 | K2 | ---
C | 9 | BK 1 ACB |  | Close | 02 | 13 | K3 | ---
C |  | BK 1 ACB |  | Open | 02 | 12 | K4 | ---
C | 10 | 24402 ACB |  | Close | 02 | 11 | K5 | ---
C |  | 24402 ACB |  | Open | 02 | 10 | K6 | ---
C | 11 | 24403 ACB |  | Close | 02 | 9 | K7 | ---
C |  | 24403 ACB |  | Open | 02 | 8 | K8 | ---
C | 12 | ADAPTIVE RELAYING |  | OFF/ON | 02 | 7 | K9 | ---
C |  | ADAPTIVE RELAYING |  | OFF/ON | 02 | 6 | K10 | ---
C | 13 | SPARE |  |  | 02 | 5 | K11 | ---
C |  | SPARE |  |  | 02 | 4 | K12 | ---
C | 14 | SPARE |  |  | 02 | 3 | K13 | ---
C |  | SPARE |  |  | 02 | 2 | K14 | ---
C | 15 | SPARE |  |  | 02 | 1 | K15 | ---
C |  | SPARE |  |  | 02 | 0 | K16 | ---

## Status
| Update: | 5/6/2019 | [7 empty] | RTU Type: | Outpost 9550 with front end ASE Protocol Translator
Stanton (JC)
Pt. | DNP TO EMS |  |  |  |  | TRW9550 to RTU
Own | Type | Pt. | Point Description | kV | Function | Type | Frame | Bit | Seq. Number | Bit Number | Comments | Rev
| I | 0 | LOCAL/REMOTE |  | LOC/REM | SS | 00 | 0 | 30 | 0
| I | 1 | BATTERY |  | NM/ALM | SS | 00 | 1 | 30 | 1
| I | 2 | F734-1 LBSW |  | CL/OP | SS | 00 | 2 | 30 | 2
| I | 3 | F734-1 LBSW |  | OP/CL | SS | 00 | 3 | 30 | 3
| I | 4 | NO 6 LBSW |  | CL/OP | SS | 00 | 4 | 30 | 4
| I | 5 | NO 6 LBSW |  | OP/CL | SS | 00 | 5 | 30 | 5
| I | 6 | F734-3 LBSW |  | CL/OP | SS | 00 | 6 | 30 | 6
| I | 7 | F734-3 LBSW |  | OP/CL | SS | 00 | 7 | 30 | 7
| I | 8 | ADAPTIVE RELAYING |  | OFF/ON | SS | 00 | 8 | 30 | 8
| I | 9 | SPARE |  |  | SS | 00 | 9 | 30 | 9
| I | 10 | SPARE |  |  | SS | 00 | 10 | 30 | 10
| I | 11 | SPARE |  |  | SS | 00 | 11 | 30 | 11
| I | 12 | SPARE |  |  | SS | 00 | 12 | 30 | 12
| I | 13 | SPARE |  |  | SS | 00 | 13 | 30 | 13
| I | 14 | SPARE |  |  | SS | 00 | 14 | 30 | 14
| I | 15 | SPARE |  |  | SS | 00 | 15 | 30 | 15
| C & I | 16 | BK 2 VCB |  | OP/CL | MCD | 00 | 01 | 00 | 0,8
| C & I | 17 | 27401 VCB |  | OP/CL | MCD | 00 | 01 | 00 | 1,9
| C & I | 18 | 27404 VCB |  | OP/CL | MCD | 00 | 01 | 00 | 2,10
| C & I | 19 | SPARE |  | OP/CL | MCD | 00 | 01 | 00 | 3,11 | Point updated to match EMS, was showing BT 12.5 VCB on legacy pt list. Field to verify.
| C & I | 20 | BK 1 ACB |  | OP/CL | MCD | 00 | 01 | 00 | 4,12
| C & I | 21 | 24402 ACB |  | OP/CL | MCD | 00 | 01 | 00 | 5,13
| C & I | 22 | 24403 ACB |  | OP/CL | MCD | 00 | 01 | 00 | 6,14
| C & I | 23 | OIL SPILL ALRM |  | NM/ALM | MCD | 00 | 01 | 00 | 7,15
| C & I | 24 | SPARE |  |  | MCD | 00 | 02 | 01 | 0,8
| C & I | 25 | SPARE |  |  | MCD | 00 | 02 | 01 | 1,9
| C & I | 26 | SPARE |  |  | MCD | 00 | 02 | 01 | 2,10
| C & I | 27 | SPARE |  |  | MCD | 00 | 02 | 01 | 3,11
| C & I | 28 | SPARE |  |  | MCD | 00 | 02 | 01 | 4,12
| C & I | 29 | SPARE |  |  | MCD | 00 | 02 | 01 | 5,13
| C & I | 30 | SPARE |  |  | MCD | 00 | 02 | 01 | 6,14
| C & I | 31 | SPARE |  |  | MCD | 00 | 02 | 01 | 7,15
| I | 32 | SPT COMM FAIL |  | NM/ALM | SPT INTERNAL INDICATION |  |  |  |  | New pt | A

## Analog
| Update: | 5/6/2019 | [6 empty] | RTU Type: | Outpost 9550 with front end ASE Protocol Translator
Stanton (JC)
Pt. | DNP to EMS |  |  |  | TRW9550 to RTU |  |  |  | Full
Own | Type | Pt. | Point Description | Function | Frame | Word | Seq. Number | Bit Number | Scale | Comments | Rev
| AI | 0 | SPARE |  | 00 | 0 | 80 | --- |  | keep index spare, was 90PCT A/D CAL | A
| AI | 1 | SPARE |  | 00 | 1 | 81 | --- |  | keep index spare, was 10PCT A/D CAL | A
| AI | 2 | 12.5 KV |  | 00 | 2 | 82 | ---
| AI | 3 | 4.8 KV |  | 00 | 3 | 83 | ---
| AI | 4 | BK1 MW | MW | 01 | 0 | 84 | --- | FS=51.84
| AI | 5 | BK1 MVAR | MVAR | 01 | 1 | 85 | --- | FS=51.84
| AI | 6 | BK2 MW | MW | 01 | 2 | 86 | --- | FS=41.472
| AI | 7 | BK2 MVAR | MVAR | 01 | 3 | 87 | --- | FS=41.472
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)