## Revisions
Alcoa (ME)
|  |  | Station Phone: |  | (717) 272-6014
|  |  | Latitude: |  | -76.3835
EMS Information |  |  | Longitude: |  | 40.2891
RTU Name: | ALCOA | ASE SPT Physical Communication Ports
FEP: | RF5 | Communication
Channel: | 46 | Port | Protocol | Local Addr | Remote Addr | Destination | Communication Circuit
Address: | 15837 | Port 1: | DNP | 15837 | 10 | FE EAST EMS 9600 Baud | MPLS via 700MHz
|  | Port 2: | Not used
PLC Information |  | Port 3: | CDC2 | 30 | 2 | RTU, 1200 baud | RS232/Modem
Processor Type: | n/a | Port 4: | Not used
Processor Memory:
Power Supply:
Rack Size:
Spare Slots:
Concept Software Rev:
RTU Information
RTU Type: | CDC 8890 with ASE Protocol Translator
Size: | Mini
Powered At: | 125VDC |  |  | Rev | Date | Description | Rev. By
Peripherals: | - |  |  | A | 2019-03-19 | Converted to Excel format. RTU being converted to DNP and cutover to MPLS over 700MHz via ASE Protocol Translator, updated baud rate and FEP/CH (old FEP/CH PF2 Ch038). Discrepancies on pt list to EMS were updated to match EMS and highlighted in red. WO#15648946 SCORES#101672 . Reviewed by H. Riley/BMcD | T. Belshe (BMcD)
Station Address | 2990 State Drive at Route 419 Lebanon, PA 17042 |  |  | B | 2019-04-18 | Created ALCOA ME CDC8890 RTU REV A.xml based on points list rev A | R.Swanbum (BMcD)

## Control
| Update: | 2019-03-19 | [7 empty] | RTU Type: | CDC 8890 with ASE Protocol Translator
Alcoa (ME)
DNP to EMS |  | RTU |  |  | Device type | CDC 2 to RTU |  | Card Slot | Inter-Connection | Customer
Type | Pt | Point Description | kV | Function |  | Seq No. | Relay No. |  |  | Termination | Comments | Rev
C | 0 | SPARE |  |  | CTRL | 0 | K0C | - | 1C1-TB1-2,3 | 1M1-1,2
[5 empty] | CTRL | 0 | K0T | - | 1C1-TB1-8,9 | 1M1-3,4
C | 1 | B91 | 69 | CLOSE | CTRL | 1 | K1C | - | 1C1-TB2-2,3 | 1M1-5,6 | Updated to match EMS, was 9142 on old pt list. | A
|  |  |  | OPEN | CTRL | 1 | K1T | - | 1C1-TB2-8,9 | 1M1-7,8
C | 2 | B92 | 69 | CLOSE | CTRL | 2 | K2C | - | 1C1-TB3-2,3 | 1M1-9,10 | Updated to match EMS, was 9242 on old pt list. | A
|  |  |  | OPEN | CTRL | 2 | K2T | - | 1C1-TB3-8,9 | 1M1-11,12
C | 3 | B142 | 69 | CLOSE | CTRL | 3 | K3C | - | 1C1-TB4-2,3 | 1M1-13,14
|  |  |  | OPEN | CTRL | 3 | K3T | - | 1C1-TB4-8,9 | 1M1-15,16
C | 4 | TEST BREAKER |  | CLOSE | CTRL | 4 | K4C | - | 1C1-TB5-2,3 | 1M1-17,18
|  |  |  | OPEN | CTRL | 4 | K4T | - | 1C1-TB5-8,9 | 1M1-19,20
C | 5 | B692 LINE BREAKER | 13.2 | CLOSE | CTRL | 5 | K5C | - | 1C1-TB6-2,3 | 1M1-21,22 | Updated to match EMS, was 8B692 on old pt list. | A
|  |  |  | OPEN | CTRL | 5 | K5T | - | 1C1-TB6-8,9 | 1M1-23,24
C | 6 | SPARE |  |  | CTRL | 6 | K6C | - | 1C1-TB7-2,3 | 1M1-25,26
[5 empty] | CTRL | 6 | K6T | - | 1C1-TB7-8,9 | 1M1-27,28
C | 7 | ADAPTIVE RELAYING |  | ON | CTRL | 7 | K7C | - | 1C1-TB8-2,3 | 1M1-29,30
|  |  |  | OFF | CTRL | 7 | K7T | - | 1C1-TB8-8,9 | 1M1-31,32

## Status
| Update: | 2019-03-19 | [6 empty] | RTU Type: | CDC 8890 with ASE Protocol Translator
Alcoa (ME)
Pt. | DNP TO EMS |  |  |  |  | CDC 2 to RTU
Own | Type | Pt. | Point Description | kV | Function | Type | Seq No. | Bit | Card Slot | Inter-Connection | Customer Termination | Comments | Rev
| I | 0 | B91 | 69 | OP/CL | 2B | 00 | 0,8 | - | 1D2-TB1-1 | 1W2-TB1-1,2 | Updated to match EMS, was 9142 on old pt list. | A
| I | 1 | B92 | 69 | OP/CL | 2B | 00 | 1,9 | - | 1D2-TB1-3 | 1W2-TB1-3,4 | Updated to match EMS, was 9242 on old pt list. | A
| I | 2 | B142 | 69 | OP/CL | 2B | 00 | 2,10 | - | 1D2-TB1-5 | 1W2-TB1-5,6
| I | 3 | B692 LINE BREAKER | 13.2 | OP/CL | 2B | 00 | 3,11 | - | 1D2-TB1-7 | 1W2-TB1-7,8 | Updated to match EMS, was 8B692 on old pt list. | A
| I | 4 | SPARE |  |  | 2B | 00 | 4,12 | - | 1D2-TB1-9 | 1W2-TB1-9,10
| I | 5 | SPARE |  |  | 2B | 00 | 5,13 | - | 1D2-TB1-11 | 1W2-TB1-11,12
| I | 6 | SPARE |  |  | 2B | 00 | 6,14 | - | 1D2-TB1-13 | 1W2-TB1-13,14
| I | 7 | TEST BREAKER |  | OP/CL | 2B | 00 | 7,15 | - | 1D2-TB1-15,16 | 1W2-TB1-15,16
| I | 8 | RTU STATUS | - | LOC/REM | SS | 30 | 00 | - | 1D1-TB1-1 | 1W1-TB1-1,2
| I | 9 | BATTERY ALARM |  | NM/ALM | SS | 30 | 01 | - | 1D1-TB1-3 | 1W1-TB1-3,4
| I | 10 | B91 LOW AIR | 69 | NM/ALM | SS | 30 | 02 | - | 1D1-TB1-5 | 1W1-TB1-5,6 | Updated to match EMS, was 9142 on old pt list. | A
| I | 11 | B92 LOW AIR | 69 | NM/ALM | SS | 30 | 03 | - | 1D1-TB1-7 | 1W1-TB1-7,8 | Updated to match EMS, was 9242 on old pt list. | A
| I | 12 | B91 TONE | 69 | NM/ALM | SS | 30 | 04 | - | 1D1-TB1-9 | 1W1-TB1-9,10 | Updated to match EMS, was 9142 on old pt list. | A
| I | 13 | B92 TONE | 69 | NM/ALM | SS | 30 | 05 | - | 1D1-TB1-11 | 1W1-TB1-11,12 | Updated to match EMS, was 9242 on old pt list. | A
| I | 14 | 91 LINE | 69 | DL/HL | SS | 30 | 06 | - | 1D1-TB1-13 | 1W1-TB1-13,14
| I | 15 | 92 LINE | 69 | DL/HL | SS | 30 | 07 | - | 1D1-TB1-15,16 | 1W1-TB1-15,16
| C & I | 16 | 69 kV BUS DIFFERENTIAL | 69 | NM/ALM | SS | 30 | 08 | - | 1D1-TB2-1 | 1W1-TB2-1,2
| C & I | 17 | RELAY TROUBLE | 13.2 | NM/ALM | SS | 30 | 09 | - | 1D1-TB2-3 | 1W1-TB2-3,4
| C & I | 18 | TR No. 1 TROUBLE | 69/13.2 | NM/ALM | SS | 30 | 10 | - | 1D1-TB2-5 | 1W1-TB2-5,6
| C & I | 19 | TR No. 2 TROUBLE | 69/13.2 | NM/ALM | SS | 30 | 11 | - | 1D1-TB2-7 | 1W1-TB2-7,8
| C & I | 20 | B142 LOW AIR |  | NM/ALM | SS | 30 | 12 | - | 1D1-TB2-9 | 1W1-TB2-9,10
| C & I | 21 | 48 VDC BATTERY ALARM |  | NM/ALM | SS | 30 | 13 | - | 1D1-TB2-11 | 1W1-TB2-11,12
| C & I | 22 | SPARE |  |  | SS | 30 | 14 | - | 1D1-TB2-13 | 1W1-TB2-13,14
| C & I | 23 | ADAPTIVE RELAYING |  | OFF/ON | SS | 30 | 15 | - | 1D1-TB2-15,16 | 1W1-TB2-15,16
| I | 24 | SPT COMM FAIL |  | NM/ALM | SPT INTERNAL INDICATION | [5 empty] | New pt | A

## Analog
| Update: | 2019-03-19 | [8 empty] | RTU Type: | CDC 8890 with ASE Protocol Translator
Alcoa (ME)
Pt. | DNP to EMS |  |  |  |  | CDC 2 to RTU |  | Full | Card | RTU Cabinet | XDCR Cabinet
Own | Type | Pt. | Point Description | kV | Function | Seq. | Scan Freq | Scale | Slot | Termination | Termination | Comments | Rev
| AI | 0 | SPARE | 69 |  | 80 | 30 |  | - |  |  | Spare "Full Scale" point upon project completion | A
| AI | 1 | SPARE | 69 |  | 81 | 30 |  | - |  |  | Spare "Zero Scale" point upon project completion | A
| AI | 2 | 91 LINE AMP A | 69 | A | 82 | 30 |  | - | 1A1-TB1-1,2 | 1X1-MT2-A2,A1 | Updated to match EMS, was 9142 on old pt list. | A
| AI | 3 | 91 LINE AMP B | 69 | A | 83 | 30 |  | - | 1A1-TB1-4,5 | 1X1-MT2-B2,B1 | Updated to match EMS, was 9142 on old pt list. | A
| AI | 4 | 91 LINE AMP C | 69 | A | 84 | 30 |  | - | 1A1-TB1-6,7 | 1X1-MT2-C2,C1 | Updated to match EMS, was 9142 on old pt list. | A
| AI | 5 | 92 LINE AL_NCW AMP A | 69 | A | 85 | 30 |  | - | 1A1-TB1-9,10 | 1X2-MT2-A2,A1 | Updated to match EMS, was 9242 on old pt list. | A
| AI | 6 | 92 LINE AL_NCW AMP B | 69 | A | 86 | 30 |  | - | 1A1-TB1-11,12 | 1X2-MT2-B2,B1 | Updated to match EMS, was 9242 on old pt list. | A
| AI | 7 | 92 LINE AL_NCW AMP C | 69 | A | 87 | 30 |  | - | 1A1-TB1-14,15 | 1X2-MT2-C2,C1 | Updated to match EMS, was 9242 on old pt list. | A
| AI | 8 | 692 LINE AMP A | 13.2 | A | 88 | 30 | 800 | - | 1A1-TB1-16,17 | 1X3-MT2-A2,A1 | Updated to match EMS, was 8B692 on old pt list. | A
| AI | 9 | 692 LINE AMP B | 13.2 | A | 89 | 30 | 800 | - | 1A1-TB1-19,20 | 1X3-MT2-B2,B1 | Updated to match EMS, was 8B692 on old pt list. | A
| AI | 10 | 692 LINE AMP C | 13.2 | A | 8A | 30 | 800 | - | 1A1-TB2-1,2 | 1X3-MT2-C2,C1 | Updated to match EMS, was 8B692 on old pt list. | A
| AI | 11 | 13.2 kV BUS | 13.2 | kV | 8B | 30 |  | - | 1A1-TB2-4,5
| AI | 12 | STATION BATTERY | 69 | A | 8C | 30 |  | - | 1A1-TB2-6,7 | NO CONNECT
| AI | 13 | 69 kV BUS | 69 | kV | 8D | 30 |  | - | 1A1-TB2-9,10 | 1X4-MT1-2,1
| AI | 14 | 91 LINE MW | 69 | MW | 8E | 10 |  | - | 1A1-TB2-11,12 | 1X1-MT1-2,1 | Updated to match EMS, was 9142 on old pt list. | A
| AI | 15 | 91 LINE MX | 69 | MVAR | 8F | 10 |  | - | 1A1-TB2-14,15 | 1X1-MT1-2A,1 | Updated to match EMS, was 9142 on old pt list. | A
| AI | 16 | 92 LINE AL_NCW MW | 69 | MW | 90 | 10 |  | - | 1A1-TB2-16,17 | 1X2-MT1-2,1 | Updated to match EMS, was 9242 on old pt list. | A
| AI | 17 | 92 LINE AL_NCW MX | 69 | MVAR | 91 | 10 |  | - | 1A1-TB2-19,20 | 1X2-MT1-2A,1 | Updated to match EMS, was 9242 on old pt list. | A
| AI | 18 | 692 LINE MW | 13.2 | MW | 92 | 10 | 28.8 | - | 1A2-TB1-1,2 | 1X3-MT1-2,1 | Updated to match EMS, was 8B692 on old pt list. | A
| AI | 19 | 692 LINE MX | 13.2 | MVAR | 93 | 10 | 28.8 | - | 1A2-TB1-4,5 | 1X3-MT1-2A,1 | Updated to match EMS, was 8B692 on old pt list. | A
Points in RTU not mapped to EMS
|  |  | SPARE |  |  | 94 | 10 |  | - | 1A2-TB1-6,7
|  |  | SPARE |  |  | 95 | 10 |  | - | 1A2-TB1-9,10
|  |  | SPARE |  |  | 96 | 10 |  | - | 1A2-TB1-11,12
|  |  | SPARE |  |  | 97 | 10 |  | - | 1A2-TB1-14,15
|  |  | SPARE |  |  | 98 | 10 |  | - | 1A2-TB1-16,17
|  |  | SPARE |  |  | 99 | 10 |  | - | 1A2-TB1-19,20
|  |  | SPARE |  |  | 9A | 10 |  | - | 1A2-TB2-1,2
|  |  | SPARE |  |  | 9B | 10 |  | - | 1A2-TB2-4,5
|  |  | SPARE |  |  | 9C | 10 |  | - | 1A2-TB2-6,7
|  |  | SPARE |  |  | 9D | 10 |  | - | 1A2-TB2-9,10
|  |  | SPARE |  |  | 9E | 10 |  | - | 1A2-TB2-11,12
|  |  | SPARE |  |  | 9F | 10 |  | - | 1A2-TB2-14,15
|  |  | SPARE |  |  | A0 | 10 |  | - | 1A2-TB2-16,17
|  |  | SPARE |  |  | A1 | 10 |  | - | 1A2-TB2-19,20
Satec PM172 meter through RTU serial port Com 2.
(Mode 4LN3)